## File Description
A description of the spreadsheets of this file is provided below.
"Load P (MW)" and "Load Q (Mvar)" spreadsheets
Column A: refers to the network bus where the load is connected to.
Columns B to Y: contain the loads' power values for each hour of the day.
"Gen Status" spreadsheet
Column A: refers to the network bus where the generator is connected to. It is worth mentioning that the generators are presented in the same order as in the network file.
Columns B to Y: contain the generators' status (as a result of the unit commitment exercise) for each hour of the day.
"Gen P (MW)" and "Gen Q (Mvar)" spreadsheets
Column A: refers to the network bus where the generator is connected to. It is worth mentioning that the generators are presented in the same order as in the network file.
Columns B to Y: contain the generators' power quantities (as a result of the dispatch exercises) for each hour of the day. It is important to state that the reactive power limits of the generators were artificially reduced to only 75% of their physical limits within the reactive power dispatch exercise, in order to prevent them from reaching their reactive power limits – thus, generators will be able to provide voltage control through reactive power support.
"Gen Vg (pu)" spreadsheet
Column A: refers to the network bus where the generator is connected to. It is worth mentioning that the generators are presented in the same order as in the network file.
Columns B to Y: contain the regulated voltage magnitude setpoint (in pu) for each hour of the day.
"Transf Tap Ratio" spreadsheet
Columns A and B: refer to the network buses where the transformer is connected to. It is worth mentioning that the transformers are presented in the same order as in the network file.
Columns C to Z: contain the transformers' winding 1 off-nominal turns ratio (in pu of winding 1 bus base voltage) for each hour of the day.
"Transf Data" spreadsheet
Columns A and B: refer to the network buses where the transformer is connected to. It is worth mentioning that the transformers are presented in the same order as in the network file.
Column C: contains the transformer's manufacture year.
Column D: contains the transformer's commissioning year.
Column E: contains the transformer's annual maximum loading (MVA). These values were indirectly estimated through power flow analyses, considering the peak and valley load of each season (in 2019).
Column F: contains the transformer's voltage ratio (kV).
Column G: contains the transformer's insulation medium.
Column H: contains the transformer's cooling system: ONAN (Oil Natural Air Natural), ONAF (Oil Natural Air Forced) and ODAF (Oil Directed Air Forced).
Column I: contains the transformer type.
Column J: contains the transformer's installation site (Indoor/Outdoor).
Column K: contains the transformer's criticallity indicator (the worst within the following), which was indirectly determined through a contingency analysis (N-1) for the 2019 winter peak scenario: A (very high) when the transformer loss leads to loss of load; B (high) when at least a transformer or line/cable gets overloaded due to the transformer loss; C (medium) when at least a transformer or line/cable exceeds 50% of its load rating; and D (low) for the remainder cases.
Column L: contains the percentage of time that the power transformer was over 50% of its rating in 2019. Such values were indirectly estimated through power flow analyses considering the peak and valley load of each season.
Column M: contains the mean loading (MVA) of each transformer directly connected to the distribution network (400/220/150 kV to 63 kV), since the number of potential customers affected by its loss is very difficult to obtain. The mean loading was indirectly estimated through power flow analyses considering the peak and valley load of each season (in 2019).
Column N: contains the undelivered energy on the 2019 winter peak scenario due to the transformer loss. These values were indirectly determined through a contingency analysis (N-1).
Column O: contains the mean loading (%) of each transformer in 2019. Such values were indirectly estimated through power flow analyses considering the peak and valley load of each season.
Column P: contains an indicative range for the value of lost load (k€/MWh).
"Lines_Cables Data" spreadsheet
Columns A and B: refer to the network buses where the line/cable is connected to. It is worth mentioning that the lines/cables are presented in the same order as in the network file.
Column C: contains the length (in km) of the line/cable.
Column D: contains the type of installation (overhead, underground or submarine) of the line/cable.
Columns E to H: contain the line/cable's ratings for summer, spring, autumn and winter, respectively.
Column I: contains the conductor cross-sectional area (mm2) of the line/cable. For the majority of overhead lines only its "designation" (e.g., Bear, Zebra...) is publicly available.
Column J: contains the line/cable's rated voltage (kV).
Column K: contains the line/cable's conductor material.
Column L: contains the line/cable's criticallity indicator, which is similar to the power transformer case (see line 33 above).
Column M: contains the percentage of time that the line/cable was over 50% of its rating in 2019. This is similar to the power transformer case (see line 34 above).
Column N: contains the number of potential customers affected by the line/cable loss, for customers directly connected to the transmission network. In other cases, no information is provided since it is very difficult to obtain. The shown values were indirectly determined through a contingency analysis (N-1) for the 2019 winter peak scenario.
Column O: contains the undelivered energy on the 2019 winter peak scenario due to the line/cable loss. This is similar to the power transformer case (see line 36 above).
Column P: contains the mean loading (%) of each line/cable in 2019. This is similar to the power transformer case (see line 37 above).
Column Q: contains an indicative range for the value of lost load (k€/MWh).
"Auxiliary Data" spreadsheet
Column A : refers to the type of distribution network (urban, semi-urban, rural).
Columns B to Y: contain the typical percentages of downward and upward flexible load for each type of distribution network and for each hour of the day.
"Downward Flexibility" spreadsheet
Column A : refers to the network bus where the load is connected to.
Columns B to Y: contain the downward flexible load values for each hour of the day.
"Upward Flexibility" spreadsheet
Column A : refers to the network bus where the load is connected to.
Columns B to Y: contain the upward flexible load values for each hour of the day.

## Load_P
bus | t1 | t2 | t3 | t4 | t5 | t6 | t7 | t8 | t9 | t10 | t11 | t12 | t13 | t14 | t15 | t16 | t17 | t18 | t19 | t20 | t21 | t22 | t23 | t24
11 | 0.661 | 0.613 | 0.586 | 0.573 | 0.572 | 0.58 | 0.625 | 0.719 | 0.825 | 0.874 | 0.876 | 0.88 | 0.856 | 0.84 | 0.85 | 0.846 | 0.851 | 0.873 | 0.942 | 0.967 | 0.965 | 0.924 | 0.849 | 0.748
13 | 2.642 | 2.451 | 2.345 | 2.291 | 2.286 | 2.321 | 2.502 | 2.875 | 3.301 | 3.496 | 3.503 | 3.522 | 3.426 | 3.36 | 3.401 | 3.383 | 3.403 | 3.494 | 3.766 | 3.87 | 3.859 | 3.695 | 3.397 | 2.993
26 | 2.246 | 2.083 | 1.993 | 1.947 | 1.943 | 1.973 | 2.127 | 2.443 | 2.806 | 2.972 | 2.978 | 2.994 | 2.912 | 2.856 | 2.891 | 2.875 | 2.893 | 2.97 | 3.201 | 3.289 | 3.281 | 3.141 | 2.888 | 2.544
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0.132 | 0.123 | 0.117 | 0.115 | 0.114 | 0.116 | 0.125 | 0.144 | 0.165 | 0.175 | 0.175 | 0.176 | 0.171 | 0.168 | 0.17 | 0.169 | 0.17 | 0.175 | 0.188 | 0.193 | 0.193 | 0.185 | 0.17 | 0.15
67 | 0.793 | 0.735 | 0.703 | 0.687 | 0.686 | 0.696 | 0.751 | 0.862 | 0.99 | 1.049 | 1.051 | 1.057 | 1.028 | 1.008 | 1.02 | 1.015 | 1.021 | 1.048 | 1.13 | 1.161 | 1.158 | 1.108 | 1.019 | 0.898
108 | 11.277 | 10.458 | 10.006 | 9.776 | 9.756 | 9.906 | 10.676 | 12.267 | 14.089 | 14.92 | 14.951 | 15.03 | 14.62 | 14.34 | 14.516 | 14.437 | 14.524 | 14.91 | 16.073 | 16.515 | 16.47 | 15.767 | 14.497 | 12.774
109 | 196.678 | 182.401 | 174.519 | 170.506 | 170.163 | 172.778 | 186.207 | 213.955 | 245.727 | 260.221 | 260.757 | 262.14 | 254.985 | 250.095 | 253.171 | 251.788 | 253.313 | 260.045 | 280.33 | 288.038 | 287.257 | 274.998 | 252.843 | 222.793
110 | 123.296 | 114.346 | 109.405 | 106.889 | 106.674 | 108.313 | 116.732 | 134.127 | 154.045 | 163.131 | 163.467 | 164.334 | 159.848 | 156.783 | 158.711 | 157.844 | 158.8 | 163.02 | 175.737 | 180.569 | 180.08 | 172.394 | 158.506 | 139.668
111 | 117.039 | 108.544 | 103.853 | 101.465 | 101.261 | 102.817 | 110.809 | 127.321 | 146.228 | 154.853 | 155.172 | 155.995 | 151.737 | 148.827 | 150.658 | 149.835 | 150.742 | 154.748 | 166.819 | 171.406 | 170.942 | 163.647 | 150.463 | 132.58
112 | 155.297 | 144.024 | 137.801 | 134.632 | 134.362 | 136.426 | 147.03 | 168.94 | 194.027 | 205.472 | 205.894 | 206.987 | 201.337 | 197.476 | 199.905 | 198.813 | 200.017 | 205.333 | 221.349 | 227.436 | 226.819 | 217.139 | 199.646 | 175.918
113 | 53.762 | 49.859 | 47.705 | 46.608 | 46.514 | 47.229 | 50.9 | 58.485 | 67.17 | 71.132 | 71.278 | 71.656 | 69.7 | 68.364 | 69.204 | 68.826 | 69.243 | 71.083 | 76.628 | 78.735 | 78.522 | 75.171 | 69.115 | 60.901
114 | 120.106 | 111.387 | 106.574 | 104.123 | 103.914 | 105.511 | 113.712 | 130.657 | 150.059 | 158.91 | 159.237 | 160.082 | 155.712 | 152.726 | 154.605 | 153.76 | 154.691 | 158.802 | 171.19 | 175.897 | 175.42 | 167.934 | 154.404 | 136.054
115 | 44.094 | 40.893 | 39.126 | 38.227 | 38.15 | 38.736 | 41.747 | 47.968 | 55.091 | 58.34 | 58.46 | 58.77 | 57.166 | 56.07 | 56.76 | 56.45 | 56.792 | 58.301 | 62.849 | 64.577 | 64.402 | 61.653 | 56.686 | 49.949
116 | 237.619 | 220.37 | 210.847 | 205.999 | 205.585 | 208.744 | 224.969 | 258.493 | 296.879 | 314.39 | 315.037 | 316.708 | 308.064 | 302.157 | 305.873 | 304.201 | 306.044 | 314.177 | 338.684 | 347.998 | 347.054 | 332.243 | 305.476 | 269.171
117 | 39.571 | 36.698 | 35.112 | 34.305 | 34.236 | 34.762 | 37.464 | 43.047 | 49.439 | 52.356 | 52.463 | 52.741 | 51.302 | 50.318 | 50.937 | 50.659 | 50.966 | 52.32 | 56.401 | 57.952 | 57.795 | 55.328 | 50.871 | 44.825
118 | 89.062 | 82.598 | 79.028 | 77.211 | 77.056 | 78.24 | 84.321 | 96.886 | 111.274 | 117.837 | 118.08 | 118.706 | 115.466 | 113.252 | 114.645 | 114.018 | 114.709 | 117.758 | 126.943 | 130.434 | 130.08 | 124.529 | 114.496 | 100.889
119 | 179.838 | 166.784 | 159.577 | 155.907 | 155.594 | 157.985 | 170.265 | 195.637 | 224.689 | 237.942 | 238.431 | 239.696 | 233.154 | 228.683 | 231.495 | 230.23 | 231.625 | 237.781 | 256.328 | 263.377 | 262.663 | 251.453 | 231.195 | 203.718
120 | 103.054 | 95.573 | 91.443 | 89.341 | 89.161 | 90.531 | 97.568 | 112.107 | 128.755 | 136.349 | 136.63 | 137.354 | 133.605 | 131.043 | 132.655 | 131.93 | 132.729 | 136.257 | 146.885 | 150.924 | 150.515 | 144.092 | 132.483 | 116.738
121 | 87.959 | 81.574 | 78.049 | 76.254 | 76.101 | 77.27 | 83.277 | 95.686 | 109.895 | 116.377 | 116.617 | 117.235 | 114.036 | 111.849 | 113.224 | 112.606 | 113.288 | 116.299 | 125.37 | 128.818 | 128.468 | 122.986 | 113.078 | 99.639
122 | 164.165 | 152.248 | 145.669 | 142.319 | 142.034 | 144.216 | 155.426 | 178.586 | 205.106 | 217.204 | 217.651 | 218.806 | 212.833 | 208.752 | 211.32 | 210.165 | 211.438 | 217.057 | 233.988 | 240.423 | 239.771 | 229.538 | 211.046 | 185.963
123 | 142.231 | 131.907 | 126.206 | 123.304 | 123.057 | 124.947 | 134.659 | 154.726 | 177.702 | 188.184 | 188.571 | 189.571 | 184.397 | 180.861 | 183.085 | 182.085 | 183.188 | 188.056 | 202.725 | 208.3 | 207.735 | 198.87 | 182.848 | 161.117
124 | 96.948 | 89.911 | 86.025 | 84.047 | 83.878 | 85.167 | 91.787 | 105.465 | 121.126 | 128.271 | 128.534 | 129.216 | 125.689 | 123.279 | 124.795 | 124.113 | 124.865 | 128.184 | 138.183 | 141.982 | 141.597 | 135.554 | 124.634 | 109.821
125 | 92.699 | 85.97 | 82.255 | 80.364 | 80.202 | 81.434 | 87.764 | 100.842 | 115.817 | 122.649 | 122.901 | 123.553 | 120.181 | 117.876 | 119.326 | 118.674 | 119.393 | 122.566 | 132.126 | 135.76 | 135.392 | 129.613 | 119.171 | 105.008
126 | 68.74 | 63.751 | 60.996 | 59.593 | 59.473 | 60.387 | 65.081 | 74.779 | 85.884 | 90.95 | 91.137 | 91.62 | 89.119 | 87.41 | 88.485 | 88.002 | 88.535 | 90.888 | 97.977 | 100.672 | 100.399 | 96.114 | 88.371 | 77.868
127 | 60.761 | 56.35 | 53.915 | 52.675 | 52.57 | 53.377 | 57.526 | 66.099 | 75.914 | 80.392 | 80.557 | 80.984 | 78.774 | 77.264 | 78.214 | 77.786 | 78.258 | 80.337 | 86.604 | 88.985 | 88.744 | 84.957 | 78.112 | 68.829
128 | 230.493 | 213.762 | 204.524 | 199.821 | 199.42 | 202.484 | 218.223 | 250.741 | 287.976 | 304.962 | 305.59 | 307.21 | 298.825 | 293.095 | 296.7 | 295.079 | 296.866 | 304.756 | 328.528 | 337.562 | 336.646 | 322.28 | 296.315 | 261.099
129 | 208.42 | 193.291 | 184.938 | 180.686 | 180.323 | 183.093 | 197.325 | 226.73 | 260.399 | 275.758 | 276.325 | 277.791 | 270.209 | 265.028 | 268.287 | 266.821 | 268.437 | 275.571 | 297.067 | 305.236 | 304.408 | 291.417 | 267.939 | 236.095
130 | 251.544 | 233.285 | 223.204 | 218.071 | 217.633 | 220.977 | 238.153 | 273.642 | 314.278 | 332.815 | 333.5 | 335.268 | 326.118 | 319.864 | 323.798 | 322.029 | 323.98 | 332.59 | 358.533 | 368.392 | 367.393 | 351.714 | 323.378 | 284.946
131 | 108.757 | 100.863 | 96.504 | 94.285 | 94.095 | 95.541 | 102.967 | 118.311 | 135.88 | 143.895 | 144.191 | 144.956 | 140.999 | 138.296 | 139.996 | 139.232 | 140.075 | 143.798 | 155.014 | 159.277 | 158.845 | 152.066 | 139.815 | 123.198
132 | 8.034 | 7.451 | 7.129 | 6.965 | 6.951 | 7.058 | 7.607 | 8.74 | 10.038 | 10.63 | 10.652 | 10.708 | 10.416 | 10.216 | 10.342 | 10.286 | 10.348 | 10.623 | 11.451 | 11.766 | 11.734 | 11.234 | 10.329 | 9.101
133 | 96.335 | 89.342 | 85.482 | 83.516 | 83.348 | 84.629 | 91.207 | 104.798 | 120.361 | 127.46 | 127.722 | 128.4 | 124.895 | 122.5 | 124.007 | 123.329 | 124.076 | 127.374 | 137.309 | 141.085 | 140.702 | 134.698 | 123.846 | 109.127
134 | 133.913 | 124.192 | 118.825 | 116.093 | 115.86 | 117.64 | 126.784 | 145.677 | 167.309 | 177.178 | 177.542 | 178.484 | 173.613 | 170.283 | 172.378 | 171.436 | 172.474 | 177.058 | 190.869 | 196.118 | 195.586 | 187.239 | 172.154 | 151.694
135 | 146.062 | 135.459 | 129.605 | 126.625 | 126.371 | 128.312 | 138.286 | 158.893 | 182.488 | 193.252 | 193.65 | 194.677 | 189.363 | 185.732 | 188.016 | 186.989 | 188.122 | 193.121 | 208.185 | 213.91 | 213.33 | 204.226 | 187.773 | 165.456
136 | 165.637 | 153.614 | 146.976 | 143.596 | 143.308 | 145.509 | 156.82 | 180.188 | 206.946 | 219.152 | 219.603 | 220.768 | 214.742 | 210.625 | 213.215 | 212.05 | 213.334 | 219.004 | 236.087 | 242.579 | 241.921 | 231.597 | 212.939 | 187.631
137 | 92.787 | 86.052 | 82.333 | 80.44 | 80.278 | 81.512 | 87.847 | 100.938 | 115.927 | 122.765 | 123.018 | 123.67 | 120.295 | 117.988 | 119.439 | 118.786 | 119.506 | 122.682 | 132.252 | 135.888 | 135.52 | 129.736 | 119.284 | 105.108
138 | 93.955 | 87.135 | 83.369 | 81.452 | 81.288 | 82.537 | 88.953 | 102.208 | 117.386 | 124.31 | 124.566 | 125.226 | 121.809 | 119.473 | 120.942 | 120.281 | 121.01 | 124.226 | 133.916 | 137.598 | 137.225 | 131.369 | 120.785 | 106.43
139 | 115.62 | 107.227 | 102.594 | 100.234 | 100.033 | 101.57 | 109.465 | 125.777 | 144.455 | 152.975 | 153.29 | 154.103 | 149.897 | 147.023 | 148.831 | 148.017 | 148.914 | 152.872 | 164.796 | 169.328 | 168.869 | 161.662 | 148.638 | 130.973
140 | 63.718 | 59.093 | 56.539 | 55.239 | 55.128 | 55.975 | 60.326 | 69.316 | 79.609 | 84.305 | 84.478 | 84.926 | 82.608 | 81.024 | 82.021 | 81.573 | 82.067 | 84.248 | 90.819 | 93.317 | 93.064 | 89.092 | 81.914 | 72.179
141 | 83.499 | 77.438 | 74.091 | 72.388 | 72.242 | 73.352 | 79.054 | 90.834 | 104.323 | 110.476 | 110.703 | 111.291 | 108.253 | 106.177 | 107.483 | 106.896 | 107.543 | 110.401 | 119.013 | 122.286 | 121.954 | 116.749 | 107.344 | 94.586
142 | 101.009 | 93.677 | 89.629 | 87.568 | 87.392 | 88.735 | 95.632 | 109.883 | 126.2 | 133.644 | 133.919 | 134.629 | 130.955 | 128.444 | 130.023 | 129.313 | 130.096 | 133.554 | 143.971 | 147.93 | 147.529 | 141.233 | 129.855 | 114.422
143 | 33.163 | 30.756 | 29.426 | 28.75 | 28.692 | 29.133 | 31.397 | 36.076 | 41.433 | 43.877 | 43.967 | 44.201 | 42.994 | 42.17 | 42.688 | 42.455 | 42.712 | 43.848 | 47.268 | 48.568 | 48.436 | 46.369 | 42.633 | 37.566
144 | 50.225 | 46.58 | 44.567 | 43.542 | 43.455 | 44.122 | 47.552 | 54.638 | 62.751 | 66.453 | 66.589 | 66.943 | 65.115 | 63.867 | 64.652 | 64.299 | 64.688 | 66.408 | 71.588 | 73.556 | 73.357 | 70.226 | 64.568 | 56.895
145 | 145.99 | 135.392 | 129.542 | 126.563 | 126.309 | 128.249 | 138.218 | 158.815 | 182.398 | 193.157 | 193.554 | 194.581 | 189.27 | 185.641 | 187.924 | 186.897 | 188.029 | 193.026 | 208.083 | 213.805 | 213.225 | 204.125 | 187.68 | 165.375
146 | 10.57 | 9.803 | 9.379 | 9.163 | 9.145 | 9.285 | 10.007 | 11.498 | 13.206 | 13.985 | 14.014 | 14.088 | 13.703 | 13.441 | 13.606 | 13.532 | 13.614 | 13.975 | 15.065 | 15.48 | 15.438 | 14.779 | 13.588 | 11.973
147 | 54.968 | 50.978 | 48.775 | 47.653 | 47.558 | 48.288 | 52.042 | 59.797 | 68.676 | 72.727 | 72.877 | 73.263 | 71.264 | 69.897 | 70.757 | 70.37 | 70.797 | 72.678 | 78.347 | 80.502 | 80.283 | 76.857 | 70.665 | 62.267
149 | 104.902 | 97.288 | 93.083 | 90.943 | 90.76 | 92.155 | 99.318 | 114.118 | 131.064 | 138.795 | 139.08 | 139.818 | 136.002 | 133.394 | 135.035 | 134.297 | 135.11 | 138.701 | 149.52 | 153.632 | 153.215 | 146.676 | 134.86 | 118.832
150 | 59.478 | 55.161 | 52.777 | 51.564 | 51.46 | 52.251 | 56.312 | 64.703 | 74.312 | 78.695 | 78.857 | 79.275 | 77.111 | 75.633 | 76.563 | 76.144 | 76.606 | 78.642 | 84.776 | 87.107 | 86.871 | 83.164 | 76.464 | 67.376
151 | 142.686 | 132.329 | 126.61 | 123.699 | 123.451 | 125.347 | 135.09 | 155.221 | 178.271 | 188.786 | 189.175 | 190.178 | 184.987 | 181.44 | 183.671 | 182.668 | 183.774 | 188.658 | 203.374 | 208.967 | 208.4 | 199.506 | 183.433 | 161.633
152 | 64.064 | 59.413 | 56.846 | 55.539 | 55.427 | 56.279 | 60.653 | 69.692 | 80.041 | 84.762 | 84.936 | 85.387 | 83.056 | 81.463 | 82.465 | 82.015 | 82.512 | 84.704 | 91.312 | 93.823 | 93.568 | 89.575 | 82.358 | 72.57
153 | 6.924 | 6.421 | 6.144 | 6.003 | 5.991 | 6.083 | 6.555 | 7.532 | 8.651 | 9.161 | 9.18 | 9.229 | 8.977 | 8.805 | 8.913 | 8.864 | 8.918 | 9.155 | 9.869 | 10.14 | 10.113 | 9.681 | 8.901 | 7.843
154 | 66.357 | 61.54 | 58.88 | 57.527 | 57.411 | 58.293 | 62.824 | 72.186 | 82.905 | 87.796 | 87.976 | 88.443 | 86.029 | 84.379 | 85.417 | 84.95 | 85.465 | 87.736 | 94.58 | 97.181 | 96.917 | 92.781 | 85.306 | 75.168
155 | 36.947 | 34.265 | 32.785 | 32.031 | 31.966 | 32.457 | 34.98 | 40.193 | 46.162 | 48.884 | 48.985 | 49.245 | 47.901 | 46.982 | 47.56 | 47.3 | 47.587 | 48.851 | 52.662 | 54.11 | 53.963 | 51.66 | 47.498 | 41.853
156 | 12.877 | 11.942 | 11.426 | 11.163 | 11.141 | 11.312 | 12.191 | 14.008 | 16.088 | 17.037 | 17.072 | 17.163 | 16.694 | 16.374 | 16.576 | 16.485 | 16.585 | 17.026 | 18.354 | 18.858 | 18.807 | 18.005 | 16.554 | 14.587
157 | 62.903 | 58.337 | 55.816 | 54.532 | 54.423 | 55.259 | 59.554 | 68.429 | 78.59 | 83.226 | 83.397 | 83.839 | 81.551 | 79.987 | 80.971 | 80.528 | 81.016 | 83.169 | 89.657 | 92.122 | 91.872 | 87.952 | 80.866 | 71.255
158 | 67.213 | 62.334 | 59.64 | 58.269 | 58.152 | 59.045 | 63.635 | 73.117 | 83.975 | 88.928 | 89.111 | 89.584 | 87.139 | 85.468 | 86.519 | 86.046 | 86.567 | 88.868 | 95.8 | 98.434 | 98.167 | 93.978 | 86.407 | 76.138
159 | 62.785 | 58.228 | 55.711 | 54.43 | 54.321 | 55.156 | 59.443 | 68.301 | 78.443 | 83.07 | 83.241 | 83.682 | 81.398 | 79.838 | 80.819 | 80.378 | 80.865 | 83.014 | 89.489 | 91.95 | 91.701 | 87.787 | 80.715 | 71.122
160 | 63.892 | 59.254 | 56.693 | 55.39 | 55.279 | 56.128 | 60.491 | 69.505 | 79.826 | 84.534 | 84.708 | 85.158 | 82.833 | 81.245 | 82.244 | 81.795 | 82.29 | 84.477 | 91.067 | 93.571 | 93.317 | 89.335 | 82.138 | 72.376
161 | 14.217 | 13.185 | 12.615 | 12.325 | 12.3 | 12.489 | 13.46 | 15.466 | 17.762 | 18.81 | 18.849 | 18.948 | 18.431 | 18.078 | 18.3 | 18.2 | 18.31 | 18.797 | 20.263 | 20.821 | 20.764 | 19.878 | 18.276 | 16.104
162 | 48.836 | 45.291 | 43.333 | 42.337 | 42.252 | 42.901 | 46.236 | 53.126 | 61.015 | 64.614 | 64.747 | 65.09 | 63.313 | 62.099 | 62.863 | 62.52 | 62.898 | 64.57 | 69.607 | 71.521 | 71.327 | 68.283 | 62.782 | 55.32
163 | 4.999 | 4.637 | 4.436 | 4.334 | 4.326 | 4.392 | 4.733 | 5.439 | 6.246 | 6.615 | 6.628 | 6.664 | 6.482 | 6.357 | 6.436 | 6.4 | 6.439 | 6.61 | 7.126 | 7.322 | 7.302 | 6.99 | 6.427 | 5.663
164 | 22.479 | 20.847 | 19.946 | 19.488 | 19.448 | 19.747 | 21.282 | 24.454 | 28.085 | 29.741 | 29.803 | 29.961 | 29.143 | 28.584 | 28.936 | 28.778 | 28.952 | 29.721 | 32.04 | 32.921 | 32.831 | 31.43 | 28.898 | 25.464
165 | 28.418 | 26.355 | 25.216 | 24.636 | 24.587 | 24.965 | 26.905 | 30.914 | 35.505 | 37.599 | 37.677 | 37.877 | 36.843 | 36.136 | 36.581 | 36.381 | 36.601 | 37.574 | 40.505 | 41.619 | 41.506 | 39.734 | 36.533 | 32.191
166 | 89.729 | 83.215 | 79.619 | 77.789 | 77.632 | 78.825 | 84.952 | 97.611 | 112.106 | 118.719 | 118.963 | 119.594 | 116.33 | 114.099 | 115.502 | 114.871 | 115.567 | 118.639 | 127.893 | 131.41 | 131.053 | 125.46 | 115.353 | 101.643
167 | 9.172 | 8.506 | 8.139 | 7.952 | 7.936 | 8.058 | 8.684 | 9.978 | 11.46 | 12.136 | 12.161 | 12.225 | 11.891 | 11.663 | 11.807 | 11.742 | 11.813 | 12.127 | 13.073 | 13.433 | 13.396 | 12.825 | 11.792 | 10.39
168 | 108.388 | 100.52 | 96.177 | 93.965 | 93.776 | 95.217 | 102.618 | 117.91 | 135.419 | 143.407 | 143.702 | 144.464 | 140.521 | 137.827 | 139.522 | 138.759 | 139.6 | 143.31 | 154.489 | 158.737 | 158.306 | 151.55 | 139.341 | 122.781
169 | 19.541 | 18.123 | 17.339 | 16.941 | 16.907 | 17.166 | 18.501 | 21.258 | 24.414 | 25.855 | 25.908 | 26.045 | 25.334 | 24.848 | 25.154 | 25.017 | 25.168 | 25.837 | 27.852 | 28.618 | 28.541 | 27.323 | 25.121 | 22.136
170 | 21.542 | 19.978 | 19.115 | 18.675 | 18.638 | 18.924 | 20.395 | 23.434 | 26.914 | 28.501 | 28.56 | 28.712 | 27.928 | 27.392 | 27.729 | 27.578 | 27.745 | 28.482 | 30.704 | 31.548 | 31.463 | 30.12 | 27.693 | 24.402
171 | 43.881 | 40.696 | 38.937 | 38.042 | 37.965 | 38.549 | 41.545 | 47.736 | 54.825 | 58.059 | 58.178 | 58.487 | 56.89 | 55.799 | 56.486 | 56.177 | 56.517 | 58.019 | 62.545 | 64.265 | 64.091 | 61.355 | 56.412 | 49.708
172 | 19.938 | 18.491 | 17.692 | 17.285 | 17.251 | 17.516 | 18.877 | 21.69 | 24.911 | 26.38 | 26.435 | 26.575 | 25.849 | 25.354 | 25.666 | 25.525 | 25.68 | 26.362 | 28.419 | 29.2 | 29.121 | 27.878 | 25.632 | 22.586
245 | 23.914 | 22.178 | 21.22 | 20.732 | 20.69 | 21.008 | 22.641 | 26.015 | 29.878 | 31.641 | 31.706 | 31.874 | 31.004 | 30.409 | 30.783 | 30.615 | 30.801 | 31.619 | 34.086 | 35.023 | 34.928 | 33.437 | 30.743 | 27.09
246 | 10.768 | 9.986 | 9.555 | 9.335 | 9.316 | 9.459 | 10.195 | 11.714 | 13.453 | 14.247 | 14.276 | 14.352 | 13.96 | 13.693 | 13.861 | 13.785 | 13.869 | 14.237 | 15.348 | 15.77 | 15.727 | 15.056 | 13.843 | 12.198
247 | 1.189 | 1.103 | 1.055 | 1.031 | 1.029 | 1.045 | 1.126 | 1.294 | 1.486 | 1.573 | 1.577 | 1.585 | 1.542 | 1.512 | 1.531 | 1.522 | 1.532 | 1.572 | 1.695 | 1.741 | 1.737 | 1.663 | 1.529 | 1.347
248 | 0.462 | 0.429 | 0.41 | 0.401 | 0.4 | 0.406 | 0.438 | 0.503 | 0.578 | 0.612 | 0.613 | 0.616 | 0.6 | 0.588 | 0.595 | 0.592 | 0.596 | 0.611 | 0.659 | 0.677 | 0.675 | 0.647 | 0.594 | 0.524
249 | 2.642 | 2.451 | 2.345 | 2.291 | 2.286 | 2.321 | 2.502 | 2.875 | 3.301 | 3.496 | 3.503 | 3.522 | 3.426 | 3.36 | 3.401 | 3.383 | 3.403 | 3.494 | 3.766 | 3.87 | 3.859 | 3.695 | 3.397 | 2.993
250 | 23.124 | 21.446 | 20.519 | 20.047 | 20.007 | 20.314 | 21.893 | 25.156 | 28.891 | 30.595 | 30.658 | 30.821 | 29.98 | 29.405 | 29.767 | 29.604 | 29.783 | 30.575 | 32.96 | 33.866 | 33.774 | 32.333 | 29.728 | 26.195
255 | 82.615 | 76.618 | 73.307 | 71.621 | 71.477 | 72.576 | 78.217 | 89.872 | 103.218 | 109.307 | 109.531 | 110.112 | 107.107 | 105.053 | 106.345 | 105.764 | 106.405 | 109.233 | 117.753 | 120.991 | 120.663 | 115.514 | 106.207 | 93.585
256 | 79.362 | 79.408 | 79.32 | 79.388 | 79.466 | 79.546 | 79.414 | 79.018 | 6.273 | 6.643 | 6.656 | 6.692 | 6.509 | 6.384 | 6.463 | 6.427 | 6.466 | 6.638 | 7.156 | 7.353 | 7.333 | 7.02 | 78.861 | 78.986
257 | 0.595 | 0.551 | 0.528 | 0.515 | 0.514 | 0.522 | 0.563 | 0.647 | 0.743 | 0.787 | 0.788 | 0.792 | 0.771 | 0.756 | 0.765 | 0.761 | 0.766 | 0.786 | 0.847 | 0.871 | 0.868 | 0.831 | 0.764 | 0.673
258 | 0.793 | 0.735 | 0.703 | 0.687 | 0.686 | 0.696 | 0.751 | 0.862 | 0.99 | 1.049 | 1.051 | 1.057 | 1.028 | 1.008 | 1.02 | 1.015 | 1.021 | 1.048 | 1.13 | 1.161 | 1.158 | 1.108 | 1.019 | 0.898
259 | 0.066 | 0.061 | 0.059 | 0.057 | 0.057 | 0.058 | 0.063 | 0.072 | 0.083 | 0.087 | 0.088 | 0.088 | 0.086 | 0.084 | 0.085 | 0.085 | 0.085 | 0.087 | 0.094 | 0.097 | 0.096 | 0.092 | 0.085 | 0.075
260 | 72.403 | 67.148 | 64.246 | 62.769 | 62.642 | 63.605 | 68.549 | 78.764 | 90.46 | 95.796 | 95.993 | 96.502 | 93.868 | 92.068 | 93.2 | 92.691 | 93.253 | 95.731 | 103.198 | 106.036 | 105.748 | 101.235 | 93.08 | 82.017
261 | 0.528 | 0.49 | 0.469 | 0.458 | 0.457 | 0.464 | 0.5 | 0.575 | 0.66 | 0.699 | 0.701 | 0.704 | 0.685 | 0.672 | 0.68 | 0.677 | 0.681 | 0.699 | 0.753 | 0.774 | 0.772 | 0.739 | 0.679 | 0.599

## Load_Q
bus | t1 | t2 | t3 | t4 | t5 | t6 | t7 | t8 | t9 | t10 | t11 | t12 | t13 | t14 | t15 | t16 | t17 | t18 | t19 | t20 | t21 | t22 | t23 | t24
11 | -0.066 | -0.061 | -0.059 | -0.057 | -0.057 | -0.058 | -0.063 | -0.072 | -0.083 | -0.087 | -0.088 | -0.088 | -0.086 | -0.084 | -0.085 | -0.085 | -0.085 | -0.087 | -0.094 | -0.097 | -0.096 | -0.092 | -0.085 | -0.075
13 | 0.793 | 0.735 | 0.703 | 0.687 | 0.686 | 0.696 | 0.751 | 0.862 | 0.99 | 1.049 | 1.051 | 1.057 | 1.028 | 1.008 | 1.02 | 1.015 | 1.021 | 1.048 | 1.13 | 1.161 | 1.158 | 1.108 | 1.019 | 0.898
26 | 0.264 | 0.245 | 0.234 | 0.229 | 0.229 | 0.232 | 0.25 | 0.287 | 0.33 | 0.35 | 0.35 | 0.352 | 0.343 | 0.336 | 0.34 | 0.338 | 0.34 | 0.349 | 0.377 | 0.387 | 0.386 | 0.369 | 0.34 | 0.299
27 | -0.3 | -0.3 | -0.3 | -0.3 | -0.3 | -0.3 | -0.3 | -0.3 | -0.3 | -0.3 | -0.3 | -0.3 | -0.3 | -0.3 | -0.3 | -0.3 | -0.3 | -0.3 | -0.3 | -0.3 | -0.3 | -0.3 | -0.3 | -0.3
28 | -0.132 | -0.123 | -0.117 | -0.115 | -0.114 | -0.116 | -0.125 | -0.144 | -0.165 | -0.175 | -0.175 | -0.176 | -0.171 | -0.168 | -0.17 | -0.169 | -0.17 | -0.175 | -0.188 | -0.193 | -0.193 | -0.185 | -0.17 | -0.15
67 | -0.066 | -0.061 | -0.059 | -0.057 | -0.057 | -0.058 | -0.063 | -0.072 | -0.083 | -0.087 | -0.088 | -0.088 | -0.086 | -0.084 | -0.085 | -0.085 | -0.085 | -0.087 | -0.094 | -0.097 | -0.096 | -0.092 | -0.085 | -0.075
108 | 1.128 | 1.046 | 1.001 | 0.978 | 0.976 | 0.991 | 1.068 | 1.227 | 1.409 | 1.492 | 1.495 | 1.503 | 1.462 | 1.434 | 1.452 | 1.444 | 1.452 | 1.491 | 1.607 | 1.651 | 1.647 | 1.577 | 1.45 | 1.277
109 | 19.668 | 18.24 | 17.452 | 17.051 | 17.016 | 17.278 | 18.621 | 21.396 | 24.573 | 26.022 | 26.076 | 26.214 | 25.498 | 25.01 | 25.317 | 25.179 | 25.331 | 26.005 | 28.033 | 28.804 | 28.726 | 27.5 | 25.284 | 22.279
110 | 12.33 | 11.435 | 10.94 | 10.689 | 10.667 | 10.831 | 11.673 | 13.413 | 15.404 | 16.313 | 16.347 | 16.433 | 15.985 | 15.678 | 15.871 | 15.784 | 15.88 | 16.302 | 17.574 | 18.057 | 18.008 | 17.239 | 15.851 | 13.967
111 | 11.704 | 10.854 | 10.385 | 10.146 | 10.126 | 10.282 | 11.081 | 12.732 | 14.623 | 15.485 | 15.517 | 15.599 | 15.174 | 14.883 | 15.066 | 14.983 | 15.074 | 15.475 | 16.682 | 17.141 | 17.094 | 16.365 | 15.046 | 13.258
112 | 15.53 | 14.402 | 13.78 | 13.463 | 13.436 | 13.643 | 14.703 | 16.894 | 19.403 | 20.547 | 20.589 | 20.699 | 20.134 | 19.748 | 19.99 | 19.881 | 20.002 | 20.533 | 22.135 | 22.744 | 22.682 | 21.714 | 19.965 | 17.592
113 | 5.376 | 4.986 | 4.77 | 4.661 | 4.651 | 4.723 | 5.09 | 5.848 | 6.717 | 7.113 | 7.128 | 7.166 | 6.97 | 6.836 | 6.92 | 6.883 | 6.924 | 7.108 | 7.663 | 7.874 | 7.852 | 7.517 | 6.911 | 6.09
114 | 12.011 | 11.139 | 10.657 | 10.412 | 10.391 | 10.551 | 11.371 | 13.066 | 15.006 | 15.891 | 15.924 | 16.008 | 15.571 | 15.273 | 15.46 | 15.376 | 15.469 | 15.88 | 17.119 | 17.59 | 17.542 | 16.793 | 15.44 | 13.605
115 | 4.409 | 4.089 | 3.913 | 3.823 | 3.815 | 3.874 | 4.175 | 4.797 | 5.509 | 5.834 | 5.846 | 5.877 | 5.717 | 5.607 | 5.676 | 5.645 | 5.679 | 5.83 | 6.285 | 6.458 | 6.44 | 6.165 | 5.669 | 4.995
116 | 23.762 | 22.037 | 21.085 | 20.6 | 20.559 | 20.874 | 22.497 | 25.849 | 29.688 | 31.439 | 31.504 | 31.671 | 30.806 | 30.216 | 30.587 | 30.42 | 30.604 | 31.418 | 33.868 | 34.8 | 34.705 | 33.224 | 30.548 | 26.917
117 | 3.957 | 3.67 | 3.511 | 3.431 | 3.424 | 3.476 | 3.746 | 4.305 | 4.944 | 5.236 | 5.246 | 5.274 | 5.13 | 5.032 | 5.094 | 5.066 | 5.097 | 5.232 | 5.64 | 5.795 | 5.779 | 5.533 | 5.087 | 4.483
118 | 8.906 | 8.26 | 7.903 | 7.721 | 7.706 | 7.824 | 8.432 | 9.689 | 11.127 | 11.784 | 11.808 | 11.871 | 11.547 | 11.325 | 11.464 | 11.402 | 11.471 | 11.776 | 12.694 | 13.043 | 13.008 | 12.453 | 11.45 | 10.089
119 | 17.984 | 16.678 | 15.958 | 15.591 | 15.559 | 15.798 | 17.026 | 19.564 | 22.469 | 23.794 | 23.843 | 23.97 | 23.315 | 22.868 | 23.15 | 23.023 | 23.162 | 23.778 | 25.633 | 26.338 | 26.266 | 25.145 | 23.12 | 20.372
120 | 10.305 | 9.557 | 9.144 | 8.934 | 8.916 | 9.053 | 9.757 | 11.211 | 12.875 | 13.635 | 13.663 | 13.735 | 13.361 | 13.104 | 13.266 | 13.193 | 13.273 | 13.626 | 14.689 | 15.092 | 15.052 | 14.409 | 13.248 | 11.674
121 | 8.796 | 8.157 | 7.805 | 7.625 | 7.61 | 7.727 | 8.328 | 9.569 | 10.99 | 11.638 | 11.662 | 11.724 | 11.404 | 11.185 | 11.322 | 11.261 | 11.329 | 11.63 | 12.537 | 12.882 | 12.847 | 12.299 | 11.308 | 9.964
122 | 16.416 | 15.225 | 14.567 | 14.232 | 14.203 | 14.422 | 15.543 | 17.859 | 20.511 | 21.72 | 21.765 | 21.881 | 21.283 | 20.875 | 21.132 | 21.016 | 21.144 | 21.706 | 23.399 | 24.042 | 23.977 | 22.954 | 21.105 | 18.596
123 | 14.223 | 13.191 | 12.621 | 12.33 | 12.306 | 12.495 | 13.466 | 15.473 | 17.77 | 18.818 | 18.857 | 18.957 | 18.44 | 18.086 | 18.309 | 18.209 | 18.319 | 18.806 | 20.273 | 20.83 | 20.774 | 19.887 | 18.285 | 16.112
124 | 9.695 | 8.991 | 8.603 | 8.405 | 8.388 | 8.517 | 9.179 | 10.546 | 12.113 | 12.827 | 12.853 | 12.922 | 12.569 | 12.328 | 12.48 | 12.411 | 12.487 | 12.818 | 13.818 | 14.198 | 14.16 | 13.555 | 12.463 | 10.982
125 | 9.27 | 8.597 | 8.226 | 8.036 | 8.02 | 8.143 | 8.776 | 10.084 | 11.582 | 12.265 | 12.29 | 12.355 | 12.018 | 11.788 | 11.933 | 11.867 | 11.939 | 12.257 | 13.213 | 13.576 | 13.539 | 12.961 | 11.917 | 10.501
126 | 6.874 | 6.375 | 6.1 | 5.959 | 5.947 | 6.039 | 6.508 | 7.478 | 8.588 | 9.095 | 9.114 | 9.162 | 8.912 | 8.741 | 8.849 | 8.8 | 8.854 | 9.089 | 9.798 | 10.067 | 10.04 | 9.611 | 8.837 | 7.787
127 | 6.076 | 5.635 | 5.392 | 5.268 | 5.257 | 5.338 | 5.753 | 6.61 | 7.591 | 8.039 | 8.056 | 8.098 | 7.877 | 7.726 | 7.821 | 7.779 | 7.826 | 8.034 | 8.66 | 8.899 | 8.874 | 8.496 | 7.811 | 6.883
128 | 23.049 | 21.376 | 20.452 | 19.982 | 19.942 | 20.248 | 21.822 | 25.074 | 28.798 | 30.496 | 30.559 | 30.721 | 29.883 | 29.31 | 29.67 | 29.508 | 29.687 | 30.476 | 32.853 | 33.756 | 33.665 | 32.228 | 29.632 | 26.11
129 | 20.842 | 19.329 | 18.494 | 18.069 | 18.032 | 18.309 | 19.733 | 22.673 | 26.04 | 27.576 | 27.633 | 27.779 | 27.021 | 26.503 | 26.829 | 26.682 | 26.844 | 27.557 | 29.707 | 30.524 | 30.441 | 29.142 | 26.794 | 23.61
130 | 25.154 | 23.329 | 22.32 | 21.807 | 21.763 | 22.098 | 23.815 | 27.364 | 31.428 | 33.282 | 33.35 | 33.527 | 32.612 | 31.986 | 32.38 | 32.203 | 32.398 | 33.259 | 35.853 | 36.839 | 36.739 | 35.171 | 32.338 | 28.495
131 | 10.876 | 10.086 | 9.65 | 9.428 | 9.41 | 9.554 | 10.297 | 11.831 | 13.588 | 14.39 | 14.419 | 14.496 | 14.1 | 13.83 | 14 | 13.923 | 14.007 | 14.38 | 15.501 | 15.928 | 15.885 | 15.207 | 13.982 | 12.32
132 | 0.803 | 0.745 | 0.713 | 0.697 | 0.695 | 0.706 | 0.761 | 0.874 | 1.004 | 1.063 | 1.065 | 1.071 | 1.042 | 1.022 | 1.034 | 1.029 | 1.035 | 1.062 | 1.145 | 1.177 | 1.173 | 1.123 | 1.033 | 0.91
133 | 9.634 | 8.934 | 8.548 | 8.352 | 8.335 | 8.463 | 9.121 | 10.48 | 12.036 | 12.746 | 12.772 | 12.84 | 12.489 | 12.25 | 12.401 | 12.333 | 12.408 | 12.737 | 13.731 | 14.108 | 14.07 | 13.47 | 12.385 | 10.913
134 | 13.391 | 12.419 | 11.883 | 11.609 | 11.586 | 11.764 | 12.678 | 14.568 | 16.731 | 17.718 | 17.754 | 17.848 | 17.361 | 17.028 | 17.238 | 17.144 | 17.247 | 17.706 | 19.087 | 19.612 | 19.559 | 18.724 | 17.215 | 15.169
135 | 8.588 | 7.965 | 7.62 | 7.445 | 7.43 | 7.544 | 8.131 | 9.342 | 10.73 | 11.363 | 11.386 | 11.446 | 11.134 | 10.92 | 11.055 | 10.994 | 11.061 | 11.355 | 12.241 | 12.577 | 12.543 | 12.008 | 11.04 | 9.728
136 | 16.564 | 15.361 | 14.698 | 14.36 | 14.331 | 14.551 | 15.682 | 18.019 | 20.695 | 21.915 | 21.96 | 22.077 | 21.474 | 21.062 | 21.321 | 21.205 | 21.333 | 21.9 | 23.609 | 24.258 | 24.192 | 23.16 | 21.294 | 18.763
137 | 9.279 | 8.605 | 8.233 | 8.044 | 8.028 | 8.151 | 8.785 | 10.094 | 11.593 | 12.277 | 12.302 | 12.367 | 12.029 | 11.799 | 11.944 | 11.879 | 11.951 | 12.268 | 13.225 | 13.589 | 13.552 | 12.974 | 11.928 | 10.511
138 | 9.395 | 8.713 | 8.337 | 8.145 | 8.129 | 8.254 | 8.895 | 10.221 | 11.739 | 12.431 | 12.457 | 12.523 | 12.181 | 11.947 | 12.094 | 12.028 | 12.101 | 12.423 | 13.392 | 13.76 | 13.723 | 13.137 | 12.079 | 10.643
139 | 11.562 | 10.723 | 10.259 | 10.023 | 10.003 | 10.157 | 10.946 | 12.578 | 14.445 | 15.298 | 15.329 | 15.41 | 14.99 | 14.702 | 14.883 | 14.802 | 14.891 | 15.287 | 16.48 | 16.933 | 16.887 | 16.166 | 14.864 | 13.097
140 | 6.372 | 5.909 | 5.654 | 5.524 | 5.513 | 5.598 | 6.033 | 6.932 | 7.961 | 8.43 | 8.448 | 8.493 | 8.261 | 8.102 | 8.202 | 8.157 | 8.207 | 8.425 | 9.082 | 9.332 | 9.306 | 8.909 | 8.191 | 7.218
141 | 8.35 | 7.744 | 7.409 | 7.239 | 7.224 | 7.335 | 7.905 | 9.083 | 10.432 | 11.048 | 11.07 | 11.129 | 10.825 | 10.618 | 10.748 | 10.69 | 10.754 | 11.04 | 11.901 | 12.229 | 12.195 | 11.675 | 10.734 | 9.459
142 | 10.101 | 9.368 | 8.963 | 8.757 | 8.739 | 8.873 | 9.563 | 10.988 | 12.62 | 13.364 | 13.392 | 13.463 | 13.095 | 12.844 | 13.002 | 12.931 | 13.01 | 13.355 | 14.397 | 14.793 | 14.753 | 14.123 | 12.985 | 11.442
143 | 2.709 | 2.512 | 2.403 | 2.348 | 2.343 | 2.379 | 2.564 | 2.946 | 3.384 | 3.584 | 3.591 | 3.61 | 3.511 | 3.444 | 3.487 | 3.467 | 3.488 | 3.581 | 3.861 | 3.967 | 3.956 | 3.787 | 3.482 | 3.068
144 | 5.023 | 4.658 | 4.457 | 4.354 | 4.345 | 4.412 | 4.755 | 5.464 | 6.275 | 6.645 | 6.659 | 6.694 | 6.512 | 6.387 | 6.465 | 6.43 | 6.469 | 6.641 | 7.159 | 7.356 | 7.336 | 7.023 | 6.457 | 5.689
145 | 14.599 | 13.539 | 12.954 | 12.656 | 12.631 | 12.825 | 13.822 | 15.881 | 18.24 | 19.316 | 19.355 | 19.458 | 18.927 | 18.564 | 18.792 | 18.69 | 18.803 | 19.303 | 20.808 | 21.38 | 21.323 | 20.413 | 18.768 | 16.537
146 | 1.057 | 0.98 | 0.938 | 0.916 | 0.914 | 0.929 | 1.001 | 1.15 | 1.321 | 1.398 | 1.401 | 1.409 | 1.37 | 1.344 | 1.361 | 1.353 | 1.361 | 1.398 | 1.507 | 1.548 | 1.544 | 1.478 | 1.359 | 1.197
147 | 5.497 | 5.098 | 4.877 | 4.765 | 4.756 | 4.829 | 5.204 | 5.98 | 6.868 | 7.273 | 7.288 | 7.326 | 7.126 | 6.99 | 7.076 | 7.037 | 7.08 | 7.268 | 7.835 | 8.05 | 8.028 | 7.686 | 7.067 | 6.227
149 | 10.49 | 9.729 | 9.308 | 9.094 | 9.076 | 9.215 | 9.932 | 11.412 | 13.106 | 13.879 | 13.908 | 13.982 | 13.6 | 13.339 | 13.503 | 13.43 | 13.511 | 13.87 | 14.952 | 15.363 | 15.322 | 14.668 | 13.486 | 11.883
150 | 5.948 | 5.516 | 5.278 | 5.156 | 5.146 | 5.225 | 5.631 | 6.47 | 7.431 | 7.869 | 7.886 | 7.928 | 7.711 | 7.563 | 7.656 | 7.614 | 7.661 | 7.864 | 8.478 | 8.711 | 8.687 | 8.316 | 7.646 | 6.738
151 | 14.269 | 13.233 | 12.661 | 12.37 | 12.345 | 12.535 | 13.509 | 15.522 | 17.827 | 18.879 | 18.917 | 19.018 | 18.499 | 18.144 | 18.367 | 18.267 | 18.377 | 18.866 | 20.337 | 20.897 | 20.84 | 19.951 | 18.343 | 16.163
152 | 6.406 | 5.941 | 5.685 | 5.554 | 5.543 | 5.628 | 6.065 | 6.969 | 8.004 | 8.476 | 8.494 | 8.539 | 8.306 | 8.146 | 8.247 | 8.201 | 8.251 | 8.47 | 9.131 | 9.382 | 9.357 | 8.957 | 8.236 | 7.257
153 | 0.692 | 0.642 | 0.614 | 0.6 | 0.599 | 0.608 | 0.656 | 0.753 | 0.865 | 0.916 | 0.918 | 0.923 | 0.898 | 0.88 | 0.891 | 0.886 | 0.892 | 0.915 | 0.987 | 1.014 | 1.011 | 0.968 | 0.89 | 0.784
154 | 6.636 | 6.154 | 5.888 | 5.753 | 5.741 | 5.829 | 6.282 | 7.219 | 8.291 | 8.78 | 8.798 | 8.844 | 8.603 | 8.438 | 8.542 | 8.495 | 8.546 | 8.774 | 9.458 | 9.718 | 9.692 | 9.278 | 8.531 | 7.517
155 | 3.695 | 3.427 | 3.278 | 3.203 | 3.197 | 3.246 | 3.498 | 4.019 | 4.616 | 4.888 | 4.898 | 4.924 | 4.79 | 4.698 | 4.756 | 4.73 | 4.759 | 4.885 | 5.266 | 5.411 | 5.396 | 5.166 | 4.75 | 4.185
156 | 1.288 | 1.194 | 1.143 | 1.116 | 1.114 | 1.131 | 1.219 | 1.401 | 1.609 | 1.704 | 1.707 | 1.716 | 1.669 | 1.637 | 1.658 | 1.649 | 1.658 | 1.703 | 1.835 | 1.886 | 1.881 | 1.8 | 1.655 | 1.459
157 | 6.29 | 5.834 | 5.582 | 5.453 | 5.442 | 5.526 | 5.955 | 6.843 | 7.859 | 8.323 | 8.34 | 8.384 | 8.155 | 7.999 | 8.097 | 8.053 | 8.102 | 8.317 | 8.966 | 9.212 | 9.187 | 8.795 | 8.087 | 7.126
158 | 6.721 | 6.233 | 5.964 | 5.827 | 5.815 | 5.905 | 6.363 | 7.312 | 8.397 | 8.893 | 8.911 | 8.958 | 8.714 | 8.547 | 8.652 | 8.605 | 8.657 | 8.887 | 9.58 | 9.843 | 9.817 | 9.398 | 8.641 | 7.614
159 | 6.279 | 5.823 | 5.571 | 5.443 | 5.432 | 5.516 | 5.944 | 6.83 | 7.844 | 8.307 | 8.324 | 8.368 | 8.14 | 7.984 | 8.082 | 8.038 | 8.086 | 8.301 | 8.949 | 9.195 | 9.17 | 8.779 | 8.071 | 7.112
160 | 6.389 | 5.925 | 5.669 | 5.539 | 5.528 | 5.613 | 6.049 | 6.95 | 7.983 | 8.453 | 8.471 | 8.516 | 8.283 | 8.124 | 8.224 | 8.179 | 8.229 | 8.448 | 9.107 | 9.357 | 9.332 | 8.933 | 8.214 | 7.238
161 | 1.422 | 1.318 | 1.261 | 1.232 | 1.23 | 1.249 | 1.346 | 1.547 | 1.776 | 1.881 | 1.885 | 1.895 | 1.843 | 1.808 | 1.83 | 1.82 | 1.831 | 1.88 | 2.026 | 2.082 | 2.076 | 1.988 | 1.828 | 1.61
162 | 4.884 | 4.529 | 4.333 | 4.234 | 4.225 | 4.29 | 4.624 | 5.313 | 6.101 | 6.461 | 6.475 | 6.509 | 6.331 | 6.21 | 6.286 | 6.252 | 6.29 | 6.457 | 6.961 | 7.152 | 7.133 | 6.828 | 6.278 | 5.532
163 | 0.5 | 0.464 | 0.444 | 0.433 | 0.433 | 0.439 | 0.473 | 0.544 | 0.625 | 0.661 | 0.663 | 0.666 | 0.648 | 0.636 | 0.644 | 0.64 | 0.644 | 0.661 | 0.713 | 0.732 | 0.73 | 0.699 | 0.643 | 0.566
164 | 2.248 | 2.085 | 1.995 | 1.949 | 1.945 | 1.975 | 2.128 | 2.445 | 2.808 | 2.974 | 2.98 | 2.996 | 2.914 | 2.858 | 2.894 | 2.878 | 2.895 | 2.972 | 3.204 | 3.292 | 3.283 | 3.143 | 2.89 | 2.546
165 | 2.842 | 2.636 | 2.522 | 2.464 | 2.459 | 2.496 | 2.691 | 3.091 | 3.551 | 3.76 | 3.768 | 3.788 | 3.684 | 3.614 | 3.658 | 3.638 | 3.66 | 3.757 | 4.05 | 4.162 | 4.151 | 3.973 | 3.653 | 3.219
166 | 8.973 | 8.322 | 7.962 | 7.779 | 7.763 | 7.883 | 8.495 | 9.761 | 11.211 | 11.872 | 11.896 | 11.959 | 11.633 | 11.41 | 11.55 | 11.487 | 11.557 | 11.864 | 12.789 | 13.141 | 13.105 | 12.546 | 11.535 | 10.164
167 | 0.917 | 0.851 | 0.814 | 0.795 | 0.794 | 0.806 | 0.868 | 0.998 | 1.146 | 1.214 | 1.216 | 1.223 | 1.189 | 1.166 | 1.181 | 1.174 | 1.181 | 1.213 | 1.307 | 1.343 | 1.34 | 1.282 | 1.179 | 1.039
168 | 10.839 | 10.052 | 9.618 | 9.397 | 9.378 | 9.522 | 10.262 | 11.791 | 13.542 | 14.341 | 14.37 | 14.446 | 14.052 | 13.783 | 13.952 | 13.876 | 13.96 | 14.331 | 15.449 | 15.874 | 15.831 | 15.155 | 13.934 | 12.278
169 | 1.954 | 1.812 | 1.734 | 1.694 | 1.691 | 1.717 | 1.85 | 2.126 | 2.441 | 2.585 | 2.591 | 2.605 | 2.533 | 2.485 | 2.515 | 2.502 | 2.517 | 2.584 | 2.785 | 2.862 | 2.854 | 2.732 | 2.512 | 2.214
170 | 2.154 | 1.998 | 1.911 | 1.868 | 1.864 | 1.892 | 2.039 | 2.343 | 2.691 | 2.85 | 2.856 | 2.871 | 2.793 | 2.739 | 2.773 | 2.758 | 2.774 | 2.848 | 3.07 | 3.155 | 3.146 | 3.012 | 2.769 | 2.44
171 | 4.388 | 4.07 | 3.894 | 3.804 | 3.797 | 3.855 | 4.155 | 4.774 | 5.482 | 5.806 | 5.818 | 5.849 | 5.689 | 5.58 | 5.649 | 5.618 | 5.652 | 5.802 | 6.254 | 6.426 | 6.409 | 6.136 | 5.641 | 4.971
172 | 1.994 | 1.849 | 1.769 | 1.729 | 1.725 | 1.752 | 1.888 | 2.169 | 2.491 | 2.638 | 2.643 | 2.657 | 2.585 | 2.535 | 2.567 | 2.553 | 2.568 | 2.636 | 2.842 | 2.92 | 2.912 | 2.788 | 2.563 | 2.259
245 | 7.531 | 6.984 | 6.683 | 6.529 | 6.516 | 6.616 | 7.13 | 8.193 | 9.409 | 9.964 | 9.985 | 10.038 | 9.764 | 9.576 | 9.694 | 9.641 | 9.7 | 9.957 | 10.734 | 11.029 | 10.999 | 10.53 | 9.682 | 8.531
246 | 2.444 | 2.267 | 2.169 | 2.119 | 2.115 | 2.147 | 2.314 | 2.659 | 3.054 | 3.234 | 3.241 | 3.258 | 3.169 | 3.108 | 3.146 | 3.129 | 3.148 | 3.232 | 3.484 | 3.58 | 3.57 | 3.418 | 3.142 | 2.769
247 | -0.066 | -0.061 | -0.059 | -0.057 | -0.057 | -0.058 | -0.063 | -0.072 | -0.083 | -0.087 | -0.088 | -0.088 | -0.086 | -0.084 | -0.085 | -0.085 | -0.085 | -0.087 | -0.094 | -0.097 | -0.096 | -0.092 | -0.085 | -0.075
248 | -0.132 | -0.123 | -0.117 | -0.115 | -0.114 | -0.116 | -0.125 | -0.144 | -0.165 | -0.175 | -0.175 | -0.176 | -0.171 | -0.168 | -0.17 | -0.169 | -0.17 | -0.175 | -0.188 | -0.193 | -0.193 | -0.185 | -0.17 | -0.15
249 | -0.528 | -0.49 | -0.469 | -0.458 | -0.457 | -0.464 | -0.5 | -0.575 | -0.66 | -0.699 | -0.701 | -0.704 | -0.685 | -0.672 | -0.68 | -0.677 | -0.681 | -0.699 | -0.753 | -0.774 | -0.772 | -0.739 | -0.679 | -0.599
250 | 2.312 | 2.145 | 2.052 | 2.005 | 2.001 | 2.031 | 2.189 | 2.516 | 2.889 | 3.06 | 3.066 | 3.082 | 2.998 | 2.94 | 2.977 | 2.96 | 2.978 | 3.057 | 3.296 | 3.387 | 3.377 | 3.233 | 2.973 | 2.619
255 | 8.261 | 7.662 | 7.331 | 7.162 | 7.148 | 7.258 | 7.822 | 8.987 | 10.322 | 10.931 | 10.953 | 11.011 | 10.711 | 10.505 | 10.635 | 10.576 | 10.64 | 10.923 | 11.775 | 12.099 | 12.066 | 11.551 | 10.621 | 9.358
256 | 6.174 | 6.177 | 6.17 | 6.176 | 6.182 | 6.188 | 6.178 | 6.147 | 0.33 | 0.35 | 0.35 | 0.352 | 0.343 | 0.336 | 0.34 | 0.338 | 0.34 | 0.349 | 0.377 | 0.387 | 0.386 | 0.369 | 6.135 | 6.144
257 | -0.33 | -0.306 | -0.293 | -0.286 | -0.286 | -0.29 | -0.313 | -0.359 | -0.413 | -0.437 | -0.438 | -0.44 | -0.428 | -0.42 | -0.425 | -0.423 | -0.425 | -0.437 | -0.471 | -0.484 | -0.482 | -0.462 | -0.425 | -0.374
258 | -0.264 | -0.245 | -0.234 | -0.229 | -0.229 | -0.232 | -0.25 | -0.287 | -0.33 | -0.35 | -0.35 | -0.352 | -0.343 | -0.336 | -0.34 | -0.338 | -0.34 | -0.349 | -0.377 | -0.387 | -0.386 | -0.369 | -0.34 | -0.299
259 | -0.33 | -0.306 | -0.293 | -0.286 | -0.286 | -0.29 | -0.313 | -0.359 | -0.413 | -0.437 | -0.438 | -0.44 | -0.428 | -0.42 | -0.425 | -0.423 | -0.425 | -0.437 | -0.471 | -0.484 | -0.482 | -0.462 | -0.425 | -0.374
260 | 22.989 | 21.321 | 20.399 | 19.93 | 19.89 | 20.196 | 21.765 | 25.009 | 28.723 | 30.417 | 30.479 | 30.641 | 29.805 | 29.233 | 29.593 | 29.431 | 29.609 | 30.396 | 32.767 | 33.668 | 33.577 | 32.144 | 29.554 | 26.042
261 | -0.264 | -0.245 | -0.234 | -0.229 | -0.229 | -0.232 | -0.25 | -0.287 | -0.33 | -0.35 | -0.35 | -0.352 | -0.343 | -0.336 | -0.34 | -0.338 | -0.34 | -0.349 | -0.377 | -0.387 | -0.386 | -0.369 | -0.34 | -0.299

## Gen Status
Bus \ Hour | 00:00 - 01:00 | 01:00 - 02:00 | 02:00 - 03:00 | 03:00 - 04:00 | 04:00 - 05:00 | 05:00 - 06:00 | 06:00 - 07:00 | 07:00 - 08:00 | 08:00 - 09:00 | 09:00 - 10:00 | 10:00 - 11:00 | 11:00 - 12:00 | 12:00 - 13:00 | 13:00 - 14:00 | 14:00 - 15:00 | 15:00 - 16:00 | 16:00 - 17:00 | 17:00 - 18:00 | 18:00 - 19:00 | 19:00 - 20:00 | 20:00 - 21:00 | 21:00 - 22:00 | 22:00 - 23:00 | 23:00 - 00:00
1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
7 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
30 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
61 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
108 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0
109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0
109 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
109 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
109 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
110 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
111 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
112 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
113 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
113 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
114 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
114 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
114 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
114 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
115 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0
115 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0
115 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
115 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
115 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
116 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
116 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
118 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
118 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
118 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
118 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
119 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
119 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
120 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
120 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
120 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
121 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
121 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
122 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
122 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
123 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
124 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
124 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
124 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
125 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
126 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
126 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
127 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
127 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
127 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
127 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
128 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
128 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
128 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0
129 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
129 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
129 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
130 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
131 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
131 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
132 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
132 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
133 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
133 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
133 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
136 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
137 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
137 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
137 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
138 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
138 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
139 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
140 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
141 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
142 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
142 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
142 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
144 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
144 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
145 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
145 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
147 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
149 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
150 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
150 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
151 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
151 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
152 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
152 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
152 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
152 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
153 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
154 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
155 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
155 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
156 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
156 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
157 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
158 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
158 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
159 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
159 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
159 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
160 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
160 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
160 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
161 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
162 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
162 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
162 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
163 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
163 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
164 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
165 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
165 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
166 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
166 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
167 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
167 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
167 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
168 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
169 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
170 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
170 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
171 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
172 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
172 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0
174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0
177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
178 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0
179 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
179 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0
181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0
181 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1
182 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
182 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
183 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
191 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
191 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1
192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1
192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0
192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0
194 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0
195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0
196 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
198 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0
198 | 0 | 0 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0
200 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
201 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
202 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1
206 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0
218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
220 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
220 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0
220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
222 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0
225 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0
227 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0
228 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0
228 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0
229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
229 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0
231 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0
233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0
234 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
235 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
236 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
237 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
238 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
239 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0
241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
242 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
251 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
252 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
253 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
254 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
255 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
262 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
263 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
264 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
265 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
266 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
267 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
268 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1
273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Gen P (MW)
bus | t1 | t2 | t3 | t4 | t5 | t6 | t7 | t8 | t9 | t10 | t11 | t12 | t13 | t14 | t15 | t16 | t17 | t18 | t19 | t20 | t21 | t22 | t23 | t24
1 | 684.31 | 865.338 | 1059.205 | 912.842 | 686.236 | 250.999 | -2.643 | -5.937 | -3.715 | -2.493 | -1.384 | 69.972 | 19.9 | 353.068 | 527.677 | 550.145 | 437.805 | -4.128 | -1.775 | 253.567 | 297.219 | 390.301 | 776.108 | 895.509
2 | 62.418 | 78.93 | 96.613 | 83.263 | 62.593 | 22.894 | -315.963 | -709.681 | -444.057 | -297.985 | -165.398 | 6.382 | 1.815 | 32.204 | 48.131 | 50.18 | 39.933 | -493.496 | -212.14 | 23.128 | 27.11 | 35.6 | 70.791 | 81.682
3 | 19.077 | 24.124 | 29.529 | 25.448 | 19.131 | 6.997 | -83.947 | -188.552 | -117.979 | -79.17 | -43.944 | 1.951 | 0.555 | 9.843 | 14.711 | 15.337 | 12.205 | -131.115 | -56.363 | 7.069 | 8.286 | 10.881 | 21.636 | 24.965
4 | 29.306 | 37.058 | 45.361 | 39.093 | 29.388 | 10.749 | -118.407 | -265.952 | -166.409 | -111.669 | -61.982 | 2.997 | 0.852 | 15.12 | 22.598 | 23.56 | 18.749 | -184.937 | -79.499 | 10.859 | 12.729 | 16.715 | 33.237 | 38.351
5 | 164.798 | 208.393 | 255.081 | 219.833 | 165.262 | 60.446 | -1.224 | -2.749 | -1.72 | -1.154 | -0.641 | 16.851 | 4.792 | 85.027 | 127.077 | 132.488 | 105.433 | -1.911 | -0.822 | 61.065 | 71.577 | 93.993 | 186.905 | 215.659
6 | 106.091 | 134.156 | 164.212 | 141.521 | 106.39 | 38.913 | 0 | 0 | 0 | 0 | 0 | 10.848 | 3.085 | 54.737 | 81.807 | 85.291 | 67.874 | 0 | 0 | 39.311 | 46.079 | 60.51 | 120.323 | 138.834
7 | 0 | 0 | 0 | 0 | 0 | 0 | -180.816 | -406.129 | -254.12 | -170.528 | -94.652 | 0 | 0 | 0 | 0 | 0 | 0 | -282.413 | -121.401 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.751 | 6.886 | 10.095 | 12.254 | 11.321 | 12.021 | 8.753 | 6.419 | 3.443 | 0.233 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.358 | 9.276 | 13.599 | 16.508 | 15.25 | 16.193 | 11.791 | 8.647 | 4.638 | 0.314 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31
30 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31
61 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 40 | 42 | 42 | 42 | 45 | 52 | 59 | 59 | 58 | 52 | 49 | 49 | 49 | 52 | 56 | 59 | 53
61 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 41 | 41 | 42 | 43 | 46 | 51 | 58 | 58 | 57 | 52 | 49 | 49 | 49 | 52 | 56 | 59 | 53
61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 3.976 | 3.776 | 3.816 | 3.631 | 3.383 | 3.195 | 2.902 | 2.367 | 1.969 | 1.523 | 1.12 | 0.763 | 0.365 | 0.155 | 0.117 | 0.086 | 0.152 | 0.205 | 0.213 | 0.274 | 0.36 | 0.454 | 0.507 | 0.661
108 | 1.826 | 1.861 | 1.999 | 1.999 | 2.136 | 2.067 | 2.033 | 2.067 | 3.446 | 4.135 | 4.135 | 3.618 | 3.79 | 3.618 | 3.446 | 3.687 | 4.135 | 4.307 | 4.48 | 4.996 | 4.48 | 3.274 | 2.24 | 1.999
109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 15.5 | 15 | 15 | 0 | 0
109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 25 | 0
109 | 23.829 | 24.141 | 23.715 | 23.744 | 23.772 | 23.715 | 23.489 | 28.051 | 28.731 | 28.532 | 28.391 | 28.561 | 28.306 | 28.079 | 27.881 | 27.909 | 28.107 | 27.994 | 28.277 | 28.561 | 28.362 | 28.164 | 28.362 | 28.136
109 | 11.242 | 10.676 | 10.791 | 10.268 | 9.566 | 9.035 | 8.204 | 6.692 | 5.567 | 4.306 | 3.167 | 2.157 | 1.032 | 0.437 | 0.33 | 0.244 | 0.43 | 0.58 | 0.602 | 0.774 | 1.017 | 1.283 | 1.433 | 1.87
109 | 1.164 | 1.186 | 1.274 | 1.274 | 1.362 | 1.318 | 1.296 | 1.318 | 2.197 | 2.636 | 2.636 | 2.307 | 2.416 | 2.307 | 2.197 | 2.35 | 2.636 | 2.746 | 2.856 | 3.185 | 2.856 | 2.087 | 1.428 | 1.274
109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.141 | 0.553 | 0.81 | 0.984 | 0.909 | 0.965 | 0.703 | 0.515 | 0.276 | 0.019 | 0 | 0 | 0 | 0 | 0 | 0
110 | 6.54 | 6.625 | 6.509 | 6.516 | 6.524 | 6.509 | 6.446 | 7.698 | 7.885 | 7.831 | 7.792 | 7.838 | 7.768 | 7.706 | 7.652 | 7.66 | 7.714 | 7.683 | 7.761 | 7.838 | 7.784 | 7.73 | 7.784 | 7.722
111 | 2.142 | 2.17 | 2.132 | 2.135 | 2.137 | 2.132 | 2.112 | 2.522 | 2.583 | 2.565 | 2.552 | 2.568 | 2.545 | 2.524 | 2.507 | 2.509 | 2.527 | 2.517 | 2.542 | 2.568 | 2.55 | 2.532 | 2.55 | 2.53
112 | 78.327 | 79.351 | 77.954 | 78.048 | 78.141 | 77.954 | 77.209 | 92.204 | 94.439 | 93.787 | 93.322 | 93.881 | 93.042 | 92.297 | 91.645 | 91.738 | 92.39 | 92.018 | 92.949 | 93.881 | 93.229 | 92.577 | 93.229 | 92.484
112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.991 | 3.898 | 5.716 | 6.938 | 6.409 | 6.806 | 4.956 | 3.634 | 1.949 | 0.132 | 0 | 0 | 0 | 0 | 0 | 0
113 | 0.226 | 0.228 | 0.224 | 0.225 | 0.225 | 0.224 | 0.222 | 0.265 | 0.272 | 0.27 | 0.269 | 0.27 | 0.268 | 0.266 | 0.264 | 0.264 | 0.266 | 0.265 | 0.268 | 0.27 | 0.268 | 0.267 | 0.268 | 0.266
113 | 0.479 | 0.488 | 0.525 | 0.525 | 0.561 | 0.543 | 0.534 | 0.543 | 0.905 | 1.085 | 1.085 | 0.95 | 0.995 | 0.95 | 0.905 | 0.968 | 1.085 | 1.131 | 1.176 | 1.312 | 1.176 | 0.859 | 0.588 | 0.525
113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.732 | 6.811 | 9.986 | 12.122 | 11.198 | 11.891 | 8.658 | 6.349 | 3.406 | 0.231 | 0 | 0 | 0 | 0 | 0 | 0
114 | 10.486 | 10.623 | 10.436 | 10.449 | 10.461 | 10.436 | 10.337 | 12.344 | 12.643 | 12.556 | 12.494 | 12.568 | 12.456 | 12.356 | 12.269 | 12.282 | 12.369 | 12.319 | 12.444 | 12.568 | 12.481 | 12.394 | 12.481 | 12.381
114 | 34.879 | 33.123 | 33.478 | 31.856 | 29.677 | 28.032 | 25.453 | 20.763 | 17.273 | 13.36 | 9.826 | 6.691 | 3.201 | 1.356 | 1.023 | 0.756 | 1.334 | 1.801 | 1.867 | 2.401 | 3.157 | 3.979 | 4.446 | 5.802
114 | 0.997 | 1.016 | 1.091 | 1.091 | 1.166 | 1.128 | 1.11 | 1.128 | 1.881 | 2.257 | 2.257 | 1.975 | 2.069 | 1.975 | 1.881 | 2.012 | 2.257 | 2.351 | 2.445 | 2.727 | 2.445 | 1.787 | 1.223 | 1.091
114 | 1.978 | 2.016 | 2.165 | 2.165 | 2.314 | 2.24 | 2.202 | 2.24 | 3.733 | 4.48 | 4.48 | 3.92 | 4.106 | 3.92 | 3.733 | 3.994 | 4.48 | 4.666 | 4.853 | 5.413 | 4.853 | 3.546 | 2.426 | 2.165
114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.156 | 0.612 | 0.898 | 1.09 | 1.007 | 1.069 | 0.778 | 0.571 | 0.306 | 0.021 | 0 | 0 | 0 | 0 | 0 | 0
115 | 0 | -18 | -18 | -18 | 0 | 0 | 0 | 9 | 10 | 11 | 14 | 0 | 0 | 0 | 0 | 9 | 0 | 17 | 16 | 15 | 13 | 11 | 0 | 0
115 | 0 | -18 | -18 | -18 | 0 | 0 | 0 | 0 | 9 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 15 | 15 | 0 | 0 | 0 | 0
115 | 0.376 | 0.381 | 0.374 | 0.375 | 0.375 | 0.374 | 0.37 | 0.442 | 0.453 | 0.45 | 0.448 | 0.45 | 0.446 | 0.443 | 0.44 | 0.44 | 0.443 | 0.442 | 0.446 | 0.45 | 0.447 | 0.444 | 0.447 | 0.444
115 | 2.276 | 2.161 | 2.185 | 2.079 | 1.936 | 1.829 | 1.661 | 1.355 | 1.127 | 0.872 | 0.641 | 0.437 | 0.209 | 0.088 | 0.067 | 0.049 | 0.087 | 0.117 | 0.122 | 0.157 | 0.206 | 0.26 | 0.29 | 0.379
115 | 0.746 | 0.76 | 0.816 | 0.816 | 0.872 | 0.844 | 0.83 | 0.844 | 1.407 | 1.688 | 1.688 | 1.477 | 1.548 | 1.477 | 1.407 | 1.506 | 1.688 | 1.759 | 1.829 | 2.04 | 1.829 | 1.337 | 0.915 | 0.816
116 | 25.783 | 26.12 | 25.661 | 25.691 | 25.722 | 25.661 | 25.415 | 30.351 | 31.087 | 30.872 | 30.719 | 30.903 | 30.627 | 30.382 | 30.167 | 30.198 | 30.413 | 30.29 | 30.597 | 30.903 | 30.689 | 30.474 | 30.689 | 30.443
116 | 0.107 | 0.109 | 0.117 | 0.117 | 0.125 | 0.121 | 0.119 | 0.121 | 0.201 | 0.241 | 0.241 | 0.211 | 0.221 | 0.211 | 0.201 | 0.215 | 0.241 | 0.251 | 0.261 | 0.291 | 0.261 | 0.191 | 0.131 | 0.117
116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076 | 0.299 | 0.438 | 0.532 | 0.491 | 0.522 | 0.38 | 0.278 | 0.149 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0
117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.611 | 2.405 | 3.526 | 4.28 | 3.954 | 4.198 | 3.057 | 2.242 | 1.202 | 0.082 | 0 | 0 | 0 | 0 | 0 | 0
118 | 14.545 | 14.736 | 14.476 | 14.493 | 14.511 | 14.476 | 14.338 | 17.122 | 17.537 | 17.416 | 17.33 | 17.434 | 17.278 | 17.14 | 17.019 | 17.036 | 17.157 | 17.088 | 17.261 | 17.434 | 17.313 | 17.192 | 17.313 | 17.174
118 | 0.356 | 0.339 | 0.342 | 0.326 | 0.303 | 0.286 | 0.26 | 0.212 | 0.177 | 0.137 | 0.1 | 0.068 | 0.033 | 0.014 | 0.01 | 0.008 | 0.014 | 0.018 | 0.019 | 0.025 | 0.032 | 0.041 | 0.045 | 0.059
118 | 1.834 | 1.868 | 2.007 | 2.007 | 2.145 | 2.076 | 2.041 | 2.076 | 3.46 | 4.152 | 4.152 | 3.633 | 3.806 | 3.633 | 3.46 | 3.702 | 4.152 | 4.325 | 4.498 | 5.017 | 4.498 | 3.287 | 2.249 | 2.007
118 | 5.973 | 6.086 | 6.537 | 6.537 | 6.988 | 6.762 | 6.65 | 6.762 | 11.271 | 13.525 | 13.525 | 11.834 | 12.398 | 11.834 | 11.271 | 12.06 | 13.525 | 14.088 | 14.652 | 16.342 | 14.652 | 10.707 | 7.326 | 6.537
119 | 1.954 | 1.98 | 1.945 | 1.947 | 1.95 | 1.945 | 1.927 | 2.301 | 2.356 | 2.34 | 2.329 | 2.343 | 2.322 | 2.303 | 2.287 | 2.289 | 2.305 | 2.296 | 2.319 | 2.343 | 2.326 | 2.31 | 2.326 | 2.308
119 | 9.981 | 9.479 | 9.58 | 9.116 | 8.492 | 8.022 | 7.284 | 5.942 | 4.943 | 3.823 | 2.812 | 1.915 | 0.916 | 0.388 | 0.293 | 0.216 | 0.382 | 0.515 | 0.534 | 0.687 | 0.903 | 1.139 | 1.272 | 1.66
119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076 | 0.299 | 0.438 | 0.532 | 0.491 | 0.522 | 0.38 | 0.278 | 0.149 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0
120 | 10.336 | 10.471 | 10.287 | 10.299 | 10.311 | 10.287 | 10.188 | 12.167 | 12.462 | 12.376 | 12.315 | 12.388 | 12.278 | 12.179 | 12.093 | 12.106 | 12.192 | 12.142 | 12.265 | 12.388 | 12.302 | 12.216 | 12.302 | 12.204
120 | 12.038 | 11.431 | 11.554 | 10.994 | 10.242 | 9.675 | 8.785 | 7.166 | 5.961 | 4.611 | 3.391 | 2.309 | 1.105 | 0.468 | 0.353 | 0.261 | 0.46 | 0.621 | 0.644 | 0.829 | 1.089 | 1.373 | 1.534 | 2.002
120 | 1.491 | 1.52 | 1.632 | 1.632 | 1.745 | 1.688 | 1.66 | 1.688 | 2.814 | 3.377 | 3.377 | 2.955 | 3.095 | 2.955 | 2.814 | 3.011 | 3.377 | 3.518 | 3.658 | 4.08 | 3.658 | 2.673 | 1.829 | 1.632
120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0.657 | 0.964 | 1.17 | 1.081 | 1.147 | 0.835 | 0.613 | 0.329 | 0.022 | 0 | 0 | 0 | 0 | 0 | 0
121 | 1.782 | 1.693 | 1.711 | 1.628 | 1.517 | 1.432 | 1.301 | 1.061 | 0.883 | 0.683 | 0.502 | 0.342 | 0.164 | 0.069 | 0.052 | 0.039 | 0.068 | 0.092 | 0.095 | 0.123 | 0.161 | 0.203 | 0.227 | 0.296
121 | 0.046 | 0.047 | 0.05 | 0.05 | 0.053 | 0.052 | 0.051 | 0.052 | 0.086 | 0.103 | 0.103 | 0.09 | 0.095 | 0.09 | 0.086 | 0.092 | 0.103 | 0.108 | 0.112 | 0.125 | 0.112 | 0.082 | 0.056 | 0.05
121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.759 | 2.987 | 4.38 | 5.316 | 4.911 | 5.215 | 3.797 | 2.785 | 1.494 | 0.101 | 0 | 0 | 0 | 0 | 0 | 0
122 | 8.006 | 8.11 | 7.968 | 7.977 | 7.987 | 7.968 | 7.891 | 9.424 | 9.652 | 9.586 | 9.538 | 9.595 | 9.51 | 9.433 | 9.367 | 9.376 | 9.443 | 9.405 | 9.5 | 9.595 | 9.529 | 9.462 | 9.529 | 9.452
122 | 39.348 | 37.367 | 37.768 | 35.938 | 33.48 | 31.624 | 28.715 | 23.423 | 19.486 | 15.072 | 11.085 | 7.549 | 3.611 | 1.53 | 1.154 | 0.853 | 1.505 | 2.031 | 2.107 | 2.708 | 3.561 | 4.489 | 5.016 | 6.546
122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004 | 0.015 | 0.022 | 0.027 | 0.025 | 0.026 | 0.019 | 0.014 | 0.007 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0
123 | 16.688 | 16.906 | 16.608 | 16.628 | 16.648 | 16.608 | 16.45 | 19.644 | 20.12 | 19.982 | 19.882 | 20.001 | 19.823 | 19.664 | 19.525 | 19.545 | 19.684 | 19.605 | 19.803 | 20.001 | 19.863 | 19.724 | 19.863 | 19.704
123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.722 | 2.838 | 4.161 | 5.051 | 4.666 | 4.954 | 3.608 | 2.646 | 1.419 | 0.096 | 0 | 0 | 0 | 0 | 0 | 0
124 | 0.038 | 0.038 | 0.037 | 0.037 | 0.037 | 0.037 | 0.037 | 0.044 | 0.045 | 0.045 | 0.045 | 0.045 | 0.045 | 0.044 | 0.044 | 0.044 | 0.044 | 0.044 | 0.045 | 0.045 | 0.045 | 0.044 | 0.045 | 0.044
124 | 59.886 | 56.871 | 57.482 | 54.695 | 50.955 | 48.13 | 43.703 | 35.649 | 29.657 | 22.939 | 16.87 | 11.489 | 5.496 | 2.328 | 1.756 | 1.298 | 2.29 | 3.092 | 3.206 | 4.122 | 5.42 | 6.832 | 7.634 | 9.962
124 | 0.068 | 0.07 | 0.075 | 0.075 | 0.08 | 0.078 | 0.076 | 0.078 | 0.129 | 0.155 | 0.155 | 0.136 | 0.142 | 0.136 | 0.129 | 0.138 | 0.155 | 0.162 | 0.168 | 0.187 | 0.168 | 0.123 | 0.084 | 0.075
125 | 4.689 | 4.453 | 4.501 | 4.282 | 3.99 | 3.768 | 3.422 | 2.791 | 2.322 | 1.796 | 1.321 | 0.9 | 0.43 | 0.182 | 0.137 | 0.102 | 0.179 | 0.242 | 0.251 | 0.323 | 0.424 | 0.535 | 0.598 | 0.78
126 | 13.493 | 13.669 | 13.429 | 13.445 | 13.461 | 13.429 | 13.3 | 15.884 | 16.269 | 16.156 | 16.076 | 16.172 | 16.028 | 15.9 | 15.787 | 15.803 | 15.916 | 15.851 | 16.012 | 16.172 | 16.06 | 15.948 | 16.06 | 15.932
126 | 5.566 | 5.286 | 5.343 | 5.084 | 4.736 | 4.474 | 4.062 | 3.314 | 2.757 | 2.132 | 1.568 | 1.068 | 0.511 | 0.216 | 0.163 | 0.121 | 0.213 | 0.287 | 0.298 | 0.383 | 0.504 | 0.635 | 0.71 | 0.926
126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.706 | 2.778 | 4.073 | 4.944 | 4.568 | 4.85 | 3.532 | 2.59 | 1.389 | 0.094 | 0 | 0 | 0 | 0 | 0 | 0
127 | 0.338 | 0.343 | 0.337 | 0.337 | 0.337 | 0.337 | 0.333 | 0.398 | 0.408 | 0.405 | 0.403 | 0.405 | 0.402 | 0.399 | 0.396 | 0.396 | 0.399 | 0.397 | 0.401 | 0.405 | 0.403 | 0.4 | 0.403 | 0.399
127 | 92.901 | 88.223 | 89.17 | 84.848 | 79.045 | 74.664 | 67.796 | 55.302 | 46.006 | 35.585 | 26.171 | 17.822 | 8.526 | 3.612 | 2.724 | 2.013 | 3.553 | 4.796 | 4.974 | 6.395 | 8.408 | 10.599 | 11.842 | 15.454
127 | 3.462 | 3.528 | 3.789 | 3.789 | 4.05 | 3.92 | 3.854 | 3.92 | 6.533 | 7.839 | 7.839 | 6.859 | 7.186 | 6.859 | 6.533 | 6.99 | 7.839 | 8.166 | 8.492 | 9.472 | 8.492 | 6.206 | 4.246 | 3.789
127 | 2.268 | 2.31 | 2.482 | 2.482 | 2.653 | 2.567 | 2.524 | 2.567 | 4.279 | 5.134 | 5.134 | 4.492 | 4.706 | 4.492 | 4.279 | 4.578 | 5.134 | 5.348 | 5.562 | 6.204 | 5.562 | 4.065 | 2.781 | 2.482
128 | 60.737 | 61.532 | 60.448 | 60.521 | 60.593 | 60.448 | 59.871 | 71.498 | 73.231 | 72.726 | 72.365 | 72.798 | 72.148 | 71.57 | 71.065 | 71.137 | 71.642 | 71.354 | 72.076 | 72.798 | 72.292 | 71.787 | 72.292 | 71.715
128 | 0.603 | 0.573 | 0.579 | 0.551 | 0.513 | 0.485 | 0.44 | 0.359 | 0.299 | 0.231 | 0.17 | 0.116 | 0.055 | 0.023 | 0.018 | 0.013 | 0.023 | 0.031 | 0.032 | 0.042 | 0.055 | 0.069 | 0.077 | 0.1
128 | 3.424 | 3.489 | 3.747 | 3.747 | 4.006 | 3.877 | 3.812 | 3.877 | 6.461 | 7.753 | 7.753 | 6.784 | 7.107 | 6.784 | 6.461 | 6.913 | 7.753 | 8.076 | 8.399 | 9.368 | 8.399 | 6.138 | 4.2 | 3.747
128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.099 | 0.388 | 0.569 | 0.691 | 0.638 | 0.678 | 0.494 | 0.362 | 0.194 | 0.013 | 0 | 0 | 0 | 0 | 0 | 0
129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 43 | 50 | 40 | 38 | 38 | 0 | 0 | 0 | 0 | 70 | 65 | 63 | 55 | 39 | 0 | 0
129 | 26.798 | 27.149 | 26.671 | 26.702 | 26.734 | 26.671 | 26.416 | 31.546 | 32.311 | 32.088 | 31.928 | 32.119 | 31.833 | 31.578 | 31.355 | 31.387 | 31.61 | 31.482 | 31.801 | 32.119 | 31.896 | 31.673 | 31.896 | 31.641
129 | 9.433 | 8.958 | 9.054 | 8.615 | 8.026 | 7.581 | 6.884 | 5.615 | 4.671 | 3.613 | 2.657 | 1.81 | 0.866 | 0.367 | 0.277 | 0.204 | 0.361 | 0.487 | 0.505 | 0.649 | 0.854 | 1.076 | 1.202 | 1.569
129 | 1.362 | 1.388 | 1.491 | 1.491 | 1.593 | 1.542 | 1.516 | 1.542 | 2.57 | 3.084 | 3.084 | 2.698 | 2.827 | 2.698 | 2.57 | 2.75 | 3.084 | 3.212 | 3.341 | 3.726 | 3.341 | 2.441 | 1.67 | 1.491
130 | 3.232 | 3.275 | 3.217 | 3.221 | 3.225 | 3.217 | 3.186 | 3.805 | 3.897 | 3.87 | 3.851 | 3.874 | 3.84 | 3.809 | 3.782 | 3.786 | 3.813 | 3.797 | 3.836 | 3.874 | 3.847 | 3.82 | 3.847 | 3.816
131 | 31.722 | 32.137 | 31.571 | 31.609 | 31.646 | 31.571 | 31.269 | 37.342 | 38.247 | 37.983 | 37.794 | 38.021 | 37.681 | 37.38 | 37.115 | 37.153 | 37.417 | 37.266 | 37.644 | 38.021 | 37.757 | 37.493 | 37.757 | 37.455
131 | 16.123 | 15.311 | 15.476 | 14.726 | 13.719 | 12.958 | 11.766 | 9.598 | 7.985 | 6.176 | 4.542 | 3.093 | 1.48 | 0.627 | 0.473 | 0.349 | 0.617 | 0.832 | 0.863 | 1.11 | 1.459 | 1.839 | 2.055 | 2.682
131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.695 | 2.733 | 4.007 | 4.865 | 4.494 | 4.772 | 3.475 | 2.548 | 1.367 | 0.093 | 0 | 0 | 0 | 0 | 0 | 0
132 | 12.478 | 12.641 | 12.419 | 12.434 | 12.449 | 12.419 | 12.3 | 14.689 | 15.045 | 14.941 | 14.867 | 14.956 | 14.822 | 14.704 | 14.6 | 14.615 | 14.719 | 14.659 | 14.808 | 14.956 | 14.852 | 14.748 | 14.852 | 14.733
132 | 5.895 | 5.599 | 5.659 | 5.384 | 5.016 | 4.738 | 4.302 | 3.509 | 2.92 | 2.258 | 1.661 | 1.131 | 0.541 | 0.229 | 0.173 | 0.128 | 0.225 | 0.304 | 0.316 | 0.406 | 0.534 | 0.673 | 0.751 | 0.981
133 | 51.529 | 52.203 | 51.284 | 51.345 | 51.406 | 51.284 | 50.794 | 60.658 | 62.129 | 61.7 | 61.394 | 61.761 | 61.21 | 60.72 | 60.291 | 60.352 | 60.781 | 60.536 | 61.148 | 61.761 | 61.332 | 60.903 | 61.332 | 60.842
133 | 34.468 | 32.732 | 33.084 | 31.48 | 29.327 | 27.701 | 25.153 | 20.518 | 17.069 | 13.203 | 9.71 | 6.612 | 3.163 | 1.34 | 1.011 | 0.747 | 1.318 | 1.779 | 1.845 | 2.373 | 3.119 | 3.932 | 4.394 | 5.734
133 | 1.24 | 1.264 | 1.357 | 1.357 | 1.451 | 1.404 | 1.381 | 1.404 | 2.34 | 2.808 | 2.808 | 2.457 | 2.574 | 2.457 | 2.34 | 2.504 | 2.808 | 2.925 | 3.042 | 3.393 | 3.042 | 2.223 | 1.521 | 1.357
293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 69.758 | 70.67 | 69.426 | 69.509 | 69.592 | 69.426 | 68.762 | 82.117 | 84.107 | 83.527 | 83.112 | 83.61 | 82.863 | 82.199 | 81.619 | 81.702 | 82.282 | 81.951 | 82.78 | 83.61 | 83.029 | 82.448 | 83.029 | 82.365
134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.046 | 0.179 | 0.263 | 0.319 | 0.295 | 0.313 | 0.228 | 0.167 | 0.09 | 0.006 | 0 | 0 | 0 | 0 | 0 | 0
136 | 2.03 | 2.056 | 2.02 | 2.022 | 2.025 | 2.02 | 2.001 | 2.389 | 2.447 | 2.43 | 2.418 | 2.433 | 2.411 | 2.392 | 2.375 | 2.377 | 2.394 | 2.384 | 2.408 | 2.433 | 2.416 | 2.399 | 2.416 | 2.396
136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.152 | 0.597 | 0.876 | 1.063 | 0.982 | 1.043 | 0.759 | 0.557 | 0.299 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0
137 | 10.599 | 10.738 | 10.549 | 10.561 | 10.574 | 10.549 | 10.448 | 12.477 | 12.779 | 12.691 | 12.628 | 12.704 | 12.59 | 12.489 | 12.401 | 12.414 | 12.502 | 12.452 | 12.578 | 12.704 | 12.615 | 12.527 | 12.615 | 12.515
137 | 11.846 | 11.249 | 11.37 | 10.819 | 10.079 | 9.52 | 8.645 | 7.052 | 5.866 | 4.537 | 3.337 | 2.272 | 1.087 | 0.461 | 0.347 | 0.257 | 0.453 | 0.612 | 0.634 | 0.815 | 1.072 | 1.351 | 1.51 | 1.97
137 | 0.342 | 0.349 | 0.375 | 0.375 | 0.401 | 0.388 | 0.381 | 0.388 | 0.646 | 0.775 | 0.775 | 0.678 | 0.711 | 0.678 | 0.646 | 0.691 | 0.775 | 0.808 | 0.84 | 0.937 | 0.84 | 0.614 | 0.42 | 0.375
138 | 2.03 | 2.056 | 2.02 | 2.022 | 2.025 | 2.02 | 2.001 | 2.389 | 2.447 | 2.43 | 2.418 | 2.433 | 2.411 | 2.392 | 2.375 | 2.377 | 2.394 | 2.384 | 2.408 | 2.433 | 2.416 | 2.399 | 2.416 | 2.396
138 | 0.472 | 0.481 | 0.516 | 0.516 | 0.552 | 0.534 | 0.525 | 0.534 | 0.89 | 1.068 | 1.068 | 0.935 | 0.979 | 0.935 | 0.89 | 0.952 | 1.068 | 1.113 | 1.157 | 1.291 | 1.157 | 0.846 | 0.579 | 0.516
138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.22 | 0.866 | 1.27 | 1.542 | 1.424 | 1.512 | 1.101 | 0.808 | 0.433 | 0.029 | 0 | 0 | 0 | 0 | 0 | 0
139 | 3.27 | 3.313 | 3.254 | 3.258 | 3.262 | 3.254 | 3.223 | 3.849 | 3.943 | 3.915 | 3.896 | 3.919 | 3.884 | 3.853 | 3.826 | 3.83 | 3.857 | 3.841 | 3.88 | 3.919 | 3.892 | 3.865 | 3.892 | 3.861
140 | 0.495 | 0.504 | 0.541 | 0.541 | 0.579 | 0.56 | 0.551 | 0.56 | 0.933 | 1.12 | 1.12 | 0.98 | 1.027 | 0.98 | 0.933 | 0.999 | 1.12 | 1.167 | 1.213 | 1.353 | 1.213 | 0.887 | 0.607 | 0.541
140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.79 | 14.907 | 21.855 | 26.529 | 24.508 | 26.024 | 18.949 | 13.896 | 7.453 | 0.505 | 0 | 0 | 0 | 0 | 0 | 0
141 | 4.585 | 4.645 | 4.564 | 4.569 | 4.574 | 4.564 | 4.52 | 5.398 | 5.529 | 5.49 | 5.463 | 5.496 | 5.447 | 5.403 | 5.365 | 5.37 | 5.409 | 5.387 | 5.441 | 5.496 | 5.458 | 5.42 | 5.458 | 5.414
142 | 7.028 | 7.12 | 6.995 | 7.003 | 7.012 | 6.995 | 6.928 | 8.274 | 8.474 | 8.416 | 8.374 | 8.424 | 8.349 | 8.282 | 8.223 | 8.232 | 8.29 | 8.257 | 8.34 | 8.424 | 8.366 | 8.307 | 8.366 | 8.299
142 | 30.738 | 29.191 | 29.504 | 28.074 | 26.154 | 24.704 | 22.432 | 18.298 | 15.222 | 11.774 | 8.659 | 5.897 | 2.821 | 1.195 | 0.901 | 0.666 | 1.175 | 1.587 | 1.646 | 2.116 | 2.782 | 3.507 | 3.918 | 5.113
142 | 2.07 | 2.109 | 2.265 | 2.265 | 2.421 | 2.343 | 2.304 | 2.343 | 3.905 | 4.686 | 4.686 | 4.101 | 4.296 | 4.101 | 3.905 | 4.179 | 4.686 | 4.882 | 5.077 | 5.663 | 5.077 | 3.71 | 2.538 | 2.265
142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004 | 0.015 | 0.022 | 0.027 | 0.025 | 0.026 | 0.019 | 0.014 | 0.007 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0
144 | 0.376 | 0.381 | 0.374 | 0.375 | 0.375 | 0.374 | 0.37 | 0.442 | 0.453 | 0.45 | 0.448 | 0.45 | 0.446 | 0.443 | 0.44 | 0.44 | 0.443 | 0.442 | 0.446 | 0.45 | 0.447 | 0.444 | 0.447 | 0.444
144 | 30.19 | 28.67 | 28.978 | 27.573 | 25.687 | 24.264 | 22.032 | 17.972 | 14.951 | 11.564 | 8.505 | 5.792 | 2.771 | 1.174 | 0.885 | 0.654 | 1.154 | 1.559 | 1.616 | 2.078 | 2.732 | 3.444 | 3.848 | 5.022
145 | 151.542 | 153.524 | 150.822 | 151.002 | 151.182 | 150.822 | 149.38 | 178.391 | 182.716 | 181.454 | 180.553 | 181.635 | 180.013 | 178.571 | 177.31 | 177.49 | 178.752 | 178.031 | 179.833 | 181.635 | 180.373 | 179.112 | 180.373 | 178.932
145 | 2.276 | 2.161 | 2.185 | 2.079 | 1.936 | 1.829 | 1.661 | 1.355 | 1.127 | 0.872 | 0.641 | 0.437 | 0.209 | 0.088 | 0.067 | 0.049 | 0.087 | 0.117 | 0.122 | 0.157 | 0.206 | 0.26 | 0.29 | 0.379
146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.539 | 2.121 | 3.11 | 3.775 | 3.487 | 3.703 | 2.696 | 1.977 | 1.061 | 0.072 | 0 | 0 | 0 | 0 | 0 | 0
147 | 1.842 | 1.866 | 1.833 | 1.835 | 1.837 | 1.833 | 1.815 | 2.168 | 2.221 | 2.205 | 2.194 | 2.207 | 2.188 | 2.17 | 2.155 | 2.157 | 2.172 | 2.164 | 2.185 | 2.207 | 2.192 | 2.177 | 2.192 | 2.175
147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.152 | 0.597 | 0.876 | 1.063 | 0.982 | 1.043 | 0.759 | 0.557 | 0.299 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0
149 | 0.413 | 0.419 | 0.411 | 0.412 | 0.412 | 0.411 | 0.408 | 0.487 | 0.498 | 0.495 | 0.493 | 0.496 | 0.491 | 0.487 | 0.484 | 0.484 | 0.488 | 0.486 | 0.491 | 0.496 | 0.492 | 0.489 | 0.492 | 0.488
149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.494 | 1.942 | 2.847 | 3.456 | 3.192 | 3.39 | 2.468 | 1.81 | 0.971 | 0.066 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6.75 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6.75 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 19.77 | 20.028 | 19.676 | 19.699 | 19.723 | 19.676 | 19.488 | 23.272 | 23.836 | 23.672 | 23.554 | 23.695 | 23.484 | 23.296 | 23.131 | 23.155 | 23.319 | 23.225 | 23.46 | 23.695 | 23.531 | 23.366 | 23.531 | 23.343
150 | 16.809 | 15.962 | 16.134 | 15.352 | 14.302 | 13.509 | 12.266 | 10.006 | 8.324 | 6.439 | 4.735 | 3.225 | 1.543 | 0.653 | 0.493 | 0.364 | 0.643 | 0.868 | 0.9 | 1.157 | 1.521 | 1.918 | 2.143 | 2.796
150 | 0.396 | 0.403 | 0.433 | 0.433 | 0.463 | 0.448 | 0.44 | 0.448 | 0.747 | 0.896 | 0.896 | 0.784 | 0.821 | 0.784 | 0.747 | 0.799 | 0.896 | 0.933 | 0.971 | 1.083 | 0.971 | 0.709 | 0.485 | 0.433
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.911 | 3.585 | 5.256 | 6.38 | 5.894 | 6.258 | 4.557 | 3.342 | 1.792 | 0.122 | 0 | 0 | 0 | 0 | 0 | 0
151 | 10.148 | 10.281 | 10.1 | 10.112 | 10.124 | 10.1 | 10.003 | 11.946 | 12.235 | 12.151 | 12.091 | 12.163 | 12.054 | 11.958 | 11.873 | 11.886 | 11.97 | 11.922 | 12.042 | 12.163 | 12.079 | 11.994 | 12.079 | 11.982
151 | 0.814 | 0.83 | 0.891 | 0.891 | 0.952 | 0.922 | 0.906 | 0.922 | 1.536 | 1.844 | 1.844 | 1.613 | 1.69 | 1.613 | 1.536 | 1.644 | 1.844 | 1.92 | 1.997 | 2.228 | 1.997 | 1.459 | 0.999 | 0.891
152 | 9.584 | 9.71 | 9.539 | 9.55 | 9.561 | 9.539 | 9.447 | 11.282 | 11.556 | 11.476 | 11.419 | 11.487 | 11.385 | 11.294 | 11.214 | 11.225 | 11.305 | 11.259 | 11.373 | 11.487 | 11.408 | 11.328 | 11.408 | 11.316
152 | 26.598 | 25.259 | 25.53 | 24.292 | 22.631 | 21.377 | 19.41 | 15.833 | 13.172 | 10.188 | 7.493 | 5.103 | 2.441 | 1.034 | 0.78 | 0.576 | 1.017 | 1.373 | 1.424 | 1.831 | 2.407 | 3.034 | 3.39 | 4.425
152 | 2.009 | 2.047 | 2.198 | 2.198 | 2.35 | 2.274 | 2.236 | 2.274 | 3.79 | 4.548 | 4.548 | 3.98 | 4.169 | 3.98 | 3.79 | 4.056 | 4.548 | 4.738 | 4.927 | 5.496 | 4.927 | 3.601 | 2.464 | 2.198
152 | 2.435 | 2.481 | 2.665 | 2.665 | 2.849 | 2.757 | 2.711 | 2.757 | 4.594 | 5.513 | 5.513 | 4.824 | 5.054 | 4.824 | 4.594 | 4.916 | 5.513 | 5.743 | 5.973 | 6.662 | 5.973 | 4.365 | 2.986 | 2.665
152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004 | 0.015 | 0.022 | 0.027 | 0.025 | 0.026 | 0.019 | 0.014 | 0.007 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0
153 | 1.179 | 1.12 | 1.132 | 1.077 | 1.003 | 0.948 | 0.86 | 0.702 | 0.584 | 0.452 | 0.332 | 0.226 | 0.108 | 0.046 | 0.035 | 0.026 | 0.045 | 0.061 | 0.063 | 0.081 | 0.107 | 0.135 | 0.15 | 0.196
153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.004 | 0.015 | 0.022 | 0.027 | 0.025 | 0.026 | 0.019 | 0.014 | 0.007 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0
154 | 1.541 | 1.561 | 1.534 | 1.535 | 1.537 | 1.534 | 1.519 | 1.814 | 1.858 | 1.845 | 1.836 | 1.847 | 1.83 | 1.816 | 1.803 | 1.805 | 1.818 | 1.81 | 1.829 | 1.847 | 1.834 | 1.821 | 1.834 | 1.819
154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.065 | 0.254 | 0.372 | 0.452 | 0.417 | 0.443 | 0.323 | 0.237 | 0.127 | 0.009 | 0 | 0 | 0 | 0 | 0 | 0
155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 | 0.113 | 0.114 | 0.112 | 0.112 | 0.112 | 0.112 | 0.111 | 0.133 | 0.136 | 0.135 | 0.134 | 0.135 | 0.134 | 0.133 | 0.132 | 0.132 | 0.133 | 0.132 | 0.134 | 0.135 | 0.134 | 0.133 | 0.134 | 0.133
155 | 70.772 | 67.209 | 67.931 | 64.638 | 60.217 | 56.879 | 51.647 | 42.13 | 35.048 | 27.109 | 19.937 | 13.577 | 6.495 | 2.752 | 2.075 | 1.534 | 2.706 | 3.654 | 3.789 | 4.872 | 6.405 | 8.074 | 9.021 | 11.773
155 | 1.507 | 1.535 | 1.649 | 1.649 | 1.763 | 1.706 | 1.677 | 1.706 | 2.843 | 3.411 | 3.411 | 2.985 | 3.127 | 2.985 | 2.843 | 3.042 | 3.411 | 3.553 | 3.696 | 4.122 | 3.696 | 2.701 | 1.848 | 1.649
156 | 63.286 | 60.1 | 60.745 | 57.801 | 53.848 | 50.863 | 46.184 | 37.673 | 31.341 | 24.242 | 17.828 | 12.141 | 5.808 | 2.46 | 1.855 | 1.371 | 2.42 | 3.267 | 3.388 | 4.356 | 5.728 | 7.22 | 8.067 | 10.528
156 | 0.708 | 0.721 | 0.774 | 0.774 | 0.828 | 0.801 | 0.788 | 0.801 | 1.335 | 1.602 | 1.602 | 1.402 | 1.469 | 1.402 | 1.335 | 1.429 | 1.602 | 1.669 | 1.736 | 1.936 | 1.736 | 1.268 | 0.868 | 0.774
157 | 6.69 | 6.778 | 6.658 | 6.666 | 6.674 | 6.658 | 6.595 | 7.875 | 8.066 | 8.011 | 7.971 | 8.019 | 7.947 | 7.883 | 7.828 | 7.836 | 7.891 | 7.859 | 7.939 | 8.019 | 7.963 | 7.907 | 7.963 | 7.899
158 | 1.052 | 1.066 | 1.047 | 1.049 | 1.05 | 1.047 | 1.037 | 1.239 | 1.269 | 1.26 | 1.254 | 1.261 | 1.25 | 1.24 | 1.231 | 1.233 | 1.241 | 1.236 | 1.249 | 1.261 | 1.253 | 1.244 | 1.253 | 1.243
158 | 17.165 | 16.301 | 16.476 | 15.677 | 14.605 | 13.796 | 12.527 | 10.218 | 8.501 | 6.575 | 4.836 | 3.293 | 1.575 | 0.667 | 0.503 | 0.372 | 0.656 | 0.886 | 0.919 | 1.182 | 1.554 | 1.958 | 2.188 | 2.855
159 | 2.669 | 2.703 | 2.656 | 2.659 | 2.662 | 2.656 | 2.63 | 3.141 | 3.217 | 3.195 | 3.179 | 3.198 | 3.17 | 3.144 | 3.122 | 3.125 | 3.148 | 3.135 | 3.167 | 3.198 | 3.176 | 3.154 | 3.176 | 3.151
159 | 45.957 | 43.643 | 44.111 | 41.973 | 39.103 | 36.935 | 33.538 | 27.357 | 22.759 | 17.604 | 12.946 | 8.816 | 4.218 | 1.787 | 1.347 | 0.996 | 1.757 | 2.373 | 2.46 | 3.163 | 4.159 | 5.243 | 5.858 | 7.645
159 | 0.175 | 0.178 | 0.192 | 0.192 | 0.205 | 0.198 | 0.195 | 0.198 | 0.33 | 0.396 | 0.396 | 0.347 | 0.363 | 0.347 | 0.33 | 0.353 | 0.396 | 0.413 | 0.429 | 0.479 | 0.429 | 0.314 | 0.215 | 0.192
159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0.657 | 0.964 | 1.17 | 1.081 | 1.147 | 0.835 | 0.613 | 0.329 | 0.022 | 0 | 0 | 0 | 0 | 0 | 0
160 | 9.885 | 10.014 | 9.838 | 9.85 | 9.861 | 9.838 | 9.744 | 11.636 | 11.918 | 11.836 | 11.777 | 11.848 | 11.742 | 11.648 | 11.566 | 11.577 | 11.66 | 11.613 | 11.73 | 11.848 | 11.765 | 11.683 | 11.765 | 11.671
160 | 52.867 | 50.205 | 50.744 | 48.284 | 44.982 | 42.489 | 38.58 | 31.471 | 26.181 | 20.25 | 14.893 | 10.142 | 4.852 | 2.055 | 1.55 | 1.146 | 2.022 | 2.729 | 2.83 | 3.639 | 4.785 | 6.031 | 6.739 | 8.794
160 | 4.178 | 4.256 | 4.572 | 4.572 | 4.887 | 4.729 | 4.651 | 4.729 | 7.882 | 9.459 | 9.459 | 8.276 | 8.67 | 8.276 | 7.882 | 8.434 | 9.459 | 9.853 | 10.247 | 11.429 | 10.247 | 7.488 | 5.123 | 4.572
161 | 61.312 | 58.225 | 58.85 | 55.998 | 52.168 | 49.276 | 44.743 | 36.498 | 30.363 | 23.485 | 17.272 | 11.762 | 5.627 | 2.384 | 1.798 | 1.329 | 2.345 | 3.165 | 3.282 | 4.22 | 5.549 | 6.995 | 7.815 | 10.199
162 | 22.062 | 22.351 | 21.957 | 21.984 | 22.01 | 21.957 | 21.748 | 25.971 | 26.601 | 26.417 | 26.286 | 26.443 | 26.207 | 25.997 | 25.814 | 25.84 | 26.024 | 25.919 | 26.181 | 26.443 | 26.26 | 26.076 | 26.26 | 26.05
162 | 11.599 | 11.015 | 11.133 | 10.593 | 9.869 | 9.322 | 8.464 | 6.905 | 5.744 | 4.443 | 3.267 | 2.225 | 1.065 | 0.451 | 0.34 | 0.251 | 0.444 | 0.599 | 0.621 | 0.798 | 1.05 | 1.323 | 1.479 | 1.929
162 | 0.213 | 0.217 | 0.233 | 0.233 | 0.249 | 0.241 | 0.237 | 0.241 | 0.402 | 0.482 | 0.482 | 0.422 | 0.442 | 0.422 | 0.402 | 0.43 | 0.482 | 0.503 | 0.523 | 0.583 | 0.523 | 0.382 | 0.261 | 0.233
163 | 59.173 | 56.194 | 56.797 | 54.044 | 50.348 | 47.557 | 43.183 | 35.225 | 29.304 | 22.666 | 16.67 | 11.352 | 5.431 | 2.301 | 1.735 | 1.282 | 2.263 | 3.055 | 3.168 | 4.073 | 5.355 | 6.751 | 7.543 | 9.843
163 | 0.51 | 0.519 | 0.558 | 0.558 | 0.596 | 0.577 | 0.568 | 0.577 | 0.962 | 1.154 | 1.154 | 1.01 | 1.058 | 1.01 | 0.962 | 1.029 | 1.154 | 1.202 | 1.251 | 1.395 | 1.251 | 0.914 | 0.625 | 0.558
164 | 0.997 | 1.016 | 1.091 | 1.091 | 1.166 | 1.128 | 1.11 | 1.128 | 1.881 | 2.257 | 2.257 | 1.975 | 2.069 | 1.975 | 1.881 | 2.012 | 2.257 | 2.351 | 2.445 | 2.727 | 2.445 | 1.787 | 1.223 | 1.091
164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.747 | 6.871 | 10.073 | 12.228 | 11.296 | 11.995 | 8.734 | 6.405 | 3.435 | 0.233 | 0 | 0 | 0 | 0 | 0 | 0
165 | 20.456 | 19.426 | 19.634 | 18.683 | 17.405 | 16.44 | 14.928 | 12.177 | 10.13 | 7.835 | 5.763 | 3.924 | 1.877 | 0.795 | 0.6 | 0.443 | 0.782 | 1.056 | 1.095 | 1.408 | 1.851 | 2.334 | 2.607 | 3.403
165 | 1.575 | 1.605 | 1.724 | 1.724 | 1.843 | 1.783 | 1.753 | 1.783 | 2.972 | 3.566 | 3.566 | 3.121 | 3.269 | 3.121 | 2.972 | 3.18 | 3.566 | 3.715 | 3.864 | 4.309 | 3.864 | 2.823 | 1.932 | 1.724
166 | 7.179 | 7.273 | 7.145 | 7.153 | 7.162 | 7.145 | 7.076 | 8.451 | 8.655 | 8.596 | 8.553 | 8.604 | 8.527 | 8.459 | 8.399 | 8.408 | 8.468 | 8.434 | 8.519 | 8.604 | 8.544 | 8.485 | 8.544 | 8.476
166 | 64.246 | 61.011 | 61.667 | 58.677 | 54.665 | 51.634 | 46.885 | 38.245 | 31.816 | 24.609 | 18.099 | 12.325 | 5.896 | 2.498 | 1.884 | 1.392 | 2.457 | 3.317 | 3.44 | 4.422 | 5.815 | 7.33 | 8.189 | 10.687
166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.008 | 0.03 | 0.044 | 0.053 | 0.049 | 0.052 | 0.038 | 0.028 | 0.015 | 0.001 | 0 | 0 | 0 | 0 | 0 | 0
167 | 0.338 | 0.343 | 0.337 | 0.337 | 0.337 | 0.337 | 0.333 | 0.398 | 0.408 | 0.405 | 0.403 | 0.405 | 0.402 | 0.399 | 0.396 | 0.396 | 0.399 | 0.397 | 0.401 | 0.405 | 0.403 | 0.4 | 0.403 | 0.399
167 | 31.917 | 30.31 | 30.636 | 29.151 | 27.157 | 25.652 | 23.292 | 19 | 15.806 | 12.226 | 8.991 | 6.123 | 2.929 | 1.241 | 0.936 | 0.692 | 1.221 | 1.648 | 1.709 | 2.197 | 2.889 | 3.641 | 4.069 | 5.309
167 | 2.808 | 2.861 | 3.073 | 3.073 | 3.285 | 3.179 | 3.126 | 3.179 | 5.298 | 6.358 | 6.358 | 5.563 | 5.828 | 5.563 | 5.298 | 5.669 | 6.358 | 6.622 | 6.887 | 7.682 | 6.887 | 5.033 | 3.444 | 3.073
168 | 1.729 | 1.752 | 1.721 | 1.723 | 1.725 | 1.721 | 1.704 | 2.035 | 2.085 | 2.07 | 2.06 | 2.072 | 2.054 | 2.037 | 2.023 | 2.025 | 2.039 | 2.031 | 2.052 | 2.072 | 2.058 | 2.043 | 2.058 | 2.041
169 | 41.844 | 39.737 | 40.164 | 38.217 | 35.603 | 33.63 | 30.536 | 24.909 | 20.722 | 16.028 | 11.788 | 8.027 | 3.84 | 1.627 | 1.227 | 0.907 | 1.6 | 2.16 | 2.24 | 2.88 | 3.787 | 4.774 | 5.334 | 6.961
169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.251 | 0.986 | 1.445 | 1.754 | 1.621 | 1.721 | 1.253 | 0.919 | 0.493 | 0.033 | 0 | 0 | 0 | 0 | 0 | 0
170 | 25.556 | 24.269 | 24.53 | 23.341 | 21.744 | 20.539 | 18.65 | 15.213 | 12.656 | 9.789 | 7.199 | 4.903 | 2.345 | 0.994 | 0.749 | 0.554 | 0.977 | 1.319 | 1.368 | 1.759 | 2.313 | 2.916 | 3.258 | 4.251
170 | 0.274 | 0.279 | 0.3 | 0.3 | 0.32 | 0.31 | 0.305 | 0.31 | 0.517 | 0.62 | 0.62 | 0.543 | 0.569 | 0.543 | 0.517 | 0.553 | 0.62 | 0.646 | 0.672 | 0.749 | 0.672 | 0.491 | 0.336 | 0.3
171 | 0.046 | 0.047 | 0.05 | 0.05 | 0.053 | 0.052 | 0.051 | 0.052 | 0.086 | 0.103 | 0.103 | 0.09 | 0.095 | 0.09 | 0.086 | 0.092 | 0.103 | 0.108 | 0.112 | 0.125 | 0.112 | 0.082 | 0.056 | 0.05
171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.456 | 1.792 | 2.628 | 3.19 | 2.947 | 3.129 | 2.278 | 1.671 | 0.896 | 0.061 | 0 | 0 | 0 | 0 | 0 | 0
172 | 14.697 | 13.957 | 14.107 | 13.423 | 12.505 | 11.812 | 10.726 | 8.749 | 7.278 | 5.63 | 4.14 | 2.82 | 1.349 | 0.571 | 0.431 | 0.318 | 0.562 | 0.759 | 0.787 | 1.012 | 1.33 | 1.677 | 1.873 | 2.445
172 | 2.511 | 2.559 | 2.748 | 2.748 | 2.938 | 2.843 | 2.795 | 2.843 | 4.738 | 5.686 | 5.686 | 4.975 | 5.212 | 4.975 | 4.738 | 5.07 | 5.686 | 5.922 | 6.159 | 6.87 | 6.159 | 4.501 | 3.08 | 2.748
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 30 | 30 | 18 | 16 | 24 | 0 | 0 | 23 | 29 | 30 | 30 | 28 | 27 | 28 | 0
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 30 | 30 | 25 | 15 | 15 | 0 | 0 | 0 | 0 | 26 | 30 | 30 | 26 | 25 | 0 | 0
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 30 | 0 | 0 | 0 | 0
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 54 | 54 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 54 | 54 | 49 | 40 | 0 | 0
174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 31 | 25 | 19 | 0 | 0
177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
178 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 29 | 29 | 29 | 28 | 18 | 18 | 15 | 15 | 23 | 25 | 29 | 29 | 28 | 28 | 28 | 28 | 20
178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 29 | 29 | 20 | 15 | 15 | 0 | 0 | 0 | 29 | 29 | 29 | 28 | 28 | 28 | 28 | 0
179 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 59 | 59 | 59 | 59 | 57 | 46 | 45 | 0 | 0 | 62 | 59 | 59 | 0 | 0 | 0 | 0 | 0
179 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 58 | 58 | 58 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 58 | 0 | 0 | 0 | 0 | 0
181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 29 | 32 | 30 | 25 | 0 | 27 | 39 | 41 | 39 | 36 | 39 | 0
181 | 0 | 0 | 0 | 0 | 0 | 23 | 23 | 30 | 32 | 32 | 33 | 30 | 30 | 31 | 30 | 25 | 33 | 28 | 40 | 41 | 39 | 37 | 40 | 37
181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 32 | 32 | 33 | 30 | 30 | 32 | 31 | 25 | 0 | 28 | 41 | 41 | 40 | 37 | 40 | 25
182 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 90 | 90 | 90 | 90 | 90 | 90 | 93 | 93 | 92 | 93 | 91 | 92 | 0 | 0 | 0 | 0 | 0
182 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 90 | 90 | 90 | 90 | 90 | 90 | 91 | 91 | 90 | 91 | 90 | 91 | 86 | 91 | 53 | 0 | 0
183 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295
187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 54 | 50 | 54 | 55 | 56 | 58 | 58 | 58 | 58 | 58 | 60 | 60 | 60 | 60 | 60 | 60 | 60
191 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 56 | 51 | 54 | 55 | 59 | 60 | 60 | 60 | 60 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 54
191 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 56 | 53 | 54 | 55 | 59 | 60 | 60 | 60 | 60 | 60 | 59 | 60 | 60 | 60 | 60 | 60 | 60
191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 169
192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 63 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 61 | 60 | 55 | 73 | 42 | 42
192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 63 | 58 | 54 | 72 | 42 | 0
192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 62 | 60 | 55 | 0 | 0 | 0
194 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 60 | 68 | 73 | 71 | 55 | 56 | 54 | 54 | 55 | 57 | 60 | 61 | 79 | 79 | 79 | 79 | 62
194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 56 | 52 | 53 | 58 | 60 | 60 | 60 | 78 | 78 | 78 | 78 | 63
194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 71 | 71 | 67 | 0 | 0 | 0
195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 72 | 56 | 0 | 0 | 0 | 0 | 0 | 68 | 67 | 71 | 71 | 71 | 70 | 0 | 0
195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 72 | 70 | 0 | 0 | 0 | 0
196 | 55 | 0 | 0 | 0 | 0 | 0 | 33 | 38 | 42 | 45 | 50 | 40 | 36 | 36 | 37 | 32 | 31 | 31 | 32 | 42 | 46 | 51 | 41 | 34
196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 32 | 32 | 32 | 31 | 31 | 31 | 32 | 40 | 45 | 49 | 40 | 32
198 | 0 | 0 | -76.5 | -76.5 | -76.5 | 0 | 39 | 75 | 75 | 61 | 75 | 50 | 50 | 55 | 0 | 0 | 0 | 68 | 75 | 75 | 75 | 75 | 70 | 0
198 | 0 | 0 | -76.5 | -76.5 | -76.5 | 0 | 39 | 75 | 75 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 75 | 75 | 75 | 75 | 71 | 0
200 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 62 | 55 | 52 | 60 | 62 | 63 | 65 | 65 | 65 | 65 | 62 | 43 | 0 | 0 | 0 | 0 | 0
201 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 62 | 55 | 52 | 58 | 60 | 61 | 63 | 63 | 65 | 65 | 62 | 61 | 45 | 45 | 58 | 52 | 45
202 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 62 | 55 | 52 | 59 | 61 | 62 | 64 | 65 | 65 | 65 | 62 | 61 | 44 | 46 | 61 | 52 | 45
203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 150 | 150 | 125 | 150 | 127 | 161
206 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 62 | 62 | 60 | 60 | 55 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 63 | 63 | 61 | 61 | 57 | 50 | 41 | 36 | 0 | 0 | 61 | 63 | 63 | 63 | 63 | 36 | 0
218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 50 | 35 | 50 | 55 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 49 | 51 | 48
218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 49 | 55 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 53 | 49
218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 50 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 53 | 41
220 | 214 | 213 | 198 | 214 | 215 | 320 | 243 | 293 | 298 | 316 | 316 | 316 | 317 | 303 | 322 | 322 | 323 | 285 | 268 | 280 | 322 | 327 | 330 | 330
220 | 0 | 0 | 0 | 0 | 0 | 0 | 241 | 294 | 297 | 316 | 316 | 316 | 316 | 303 | 323 | 322 | 322 | 284 | 267 | 280 | 322 | 327 | 330 | 0
220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 295 | 315 | 315 | 315 | 315 | 302 | 322 | 321 | 322 | 284 | 266 | 280 | 322 | 327 | 0 | 0
222 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 270 | 236 | 255 | 286 | 315 | 315 | 350 | 335 | 328 | 274 | 237 | 247 | 237 | 286 | 0 | 0 | 0
225 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 179 | 154 | 135 | 177 | 181 | 187 | 115 | 172 | 134 | 132 | 190 | 191 | 191 | 171 | 156 | 144 | 0
227 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 98 | 102 | 101 | 74 | 60 | 60 | 60 | 60 | 60 | 60 | 102 | 104 | 104 | 105 | 106 | 60 | 60
227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 104 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 108 | 106 | 102 | 0 | 0 | 0
228 | 0 | 0 | -128 | 0 | 0 | 0 | 0 | 0 | 64 | 101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 104 | 104 | 103 | 99 | 0 | 0
228 | 0 | -128 | -128 | -128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 105 | 105 | 91 | 0 | 0 | 0
229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
229 | -305 | -311 | -330.5 | -320.5 | -289 | -16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230 | 0 | 0 | 0 | 0 | 0 | 0 | 110 | 110 | 125 | 149 | 213 | 120 | 113 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0
231 | 0 | 0 | -130.5 | -130.5 | 0 | 0 | 0 | 123 | 120 | 120 | 70 | 82 | 90 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 130 | 0 | 0
231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 252 | 249 | 0 | 0 | 0 | 0 | 0
233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245 | 250 | 250 | 246 | 158 | 158 | 0 | 0 | 0 | 221 | 245 | 248 | 191 | 201 | 215 | 158 | 0
234 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295
235 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295
236 | 295 | 294 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295
237 | 287 | 149 | 123 | 122 | 170 | 253 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288
238 | 286 | 156 | 123 | 122 | 171 | 252 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 288 | 287 | 287 | 288 | 288 | 288 | 288 | 288 | 288 | 288
239 | 333.9215 | 261.7658 | 237.3118 | 261.5322 | 269.9286 | 316.939 | 238.276 | 267.2318 | 250.7643 | 307.4184 | 281.9979 | 337.8432 | 335.5496 | 379.5997 | 370.7063 | 359.6569 | 296.0394 | 244.6493 | 279.3819 | 237.556 | 298.3246 | 308.6895 | 307.1855 | 298.0155
240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 238 | 259 | 238 | 0 | 0 | 0 | 0
241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 379 | 350 | 344 | 361 | 367 | 356 | 304 | 266 | 290 | 248 | 329 | 337 | 273 | 317 | 290 | 0 | 0
242 | 326 | 248 | 248 | 248 | 248 | 312 | 256 | 392 | 350 | 342 | 361 | 367 | 356 | 302 | 266 | 290 | 248 | 329 | 337 | 273 | 318 | 315 | 413 | 280
243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250 | 18.943 | 19.191 | 18.853 | 18.875 | 18.898 | 18.853 | 18.673 | 22.299 | 22.839 | 22.682 | 22.569 | 22.704 | 22.502 | 22.321 | 22.164 | 22.186 | 22.344 | 22.254 | 22.479 | 22.704 | 22.547 | 22.389 | 22.547 | 22.366
251 | 31.259 | 29.685 | 30.004 | 28.55 | 26.597 | 25.123 | 22.812 | 18.608 | 15.48 | 11.974 | 8.806 | 5.997 | 2.869 | 1.215 | 0.916 | 0.677 | 1.195 | 1.614 | 1.674 | 2.152 | 2.829 | 3.566 | 3.985 | 5.2
252 | 49.521 | 47.028 | 47.533 | 45.229 | 42.136 | 39.8 | 36.139 | 29.479 | 24.524 | 18.969 | 13.951 | 9.5 | 4.545 | 1.925 | 1.452 | 1.073 | 1.894 | 2.557 | 2.651 | 3.409 | 4.482 | 5.65 | 6.312 | 8.238
253 | 33.618 | 31.925 | 32.268 | 30.704 | 28.604 | 27.018 | 24.533 | 20.012 | 16.648 | 12.877 | 9.47 | 6.449 | 3.085 | 1.307 | 0.986 | 0.728 | 1.286 | 1.736 | 1.8 | 2.314 | 3.043 | 3.835 | 4.285 | 5.592
254 | 70.745 | 67.183 | 67.904 | 64.613 | 60.194 | 56.857 | 51.627 | 42.113 | 35.034 | 27.099 | 19.929 | 13.572 | 6.493 | 2.75 | 2.074 | 1.533 | 2.705 | 3.652 | 3.787 | 4.87 | 6.403 | 8.071 | 9.018 | 11.768
255 | 76.222 | 77.219 | 75.86 | 75.95 | 76.041 | 75.86 | 75.135 | 89.726 | 91.902 | 91.267 | 90.814 | 91.358 | 90.542 | 89.817 | 89.183 | 89.273 | 89.908 | 89.545 | 90.452 | 91.358 | 90.723 | 90.089 | 90.723 | 89.998
262 | 65.398 | 62.105 | 62.772 | 59.729 | 55.644 | 52.56 | 47.725 | 38.93 | 32.386 | 25.05 | 18.423 | 12.546 | 6.002 | 2.543 | 1.917 | 1.417 | 2.501 | 3.376 | 3.501 | 4.502 | 5.919 | 7.461 | 8.336 | 10.879
263 | 36.469 | 34.633 | 35.005 | 33.308 | 31.03 | 29.31 | 26.614 | 21.71 | 18.06 | 13.969 | 10.274 | 6.996 | 3.347 | 1.418 | 1.069 | 0.79 | 1.395 | 1.883 | 1.952 | 2.51 | 3.301 | 4.161 | 4.649 | 6.067
264 | 75.434 | 71.636 | 72.405 | 68.895 | 64.184 | 60.626 | 55.049 | 44.904 | 37.356 | 28.895 | 21.25 | 14.471 | 6.923 | 2.933 | 2.212 | 1.635 | 2.885 | 3.894 | 4.039 | 5.192 | 6.827 | 8.606 | 9.616 | 12.548
265 | 29.998 | 28.488 | 28.793 | 27.398 | 25.524 | 24.109 | 21.891 | 17.857 | 14.856 | 11.491 | 8.451 | 5.755 | 2.753 | 1.166 | 0.879 | 0.65 | 1.147 | 1.549 | 1.606 | 2.065 | 2.715 | 3.422 | 3.824 | 4.99
266 | 38.389 | 36.456 | 36.847 | 35.061 | 32.663 | 30.853 | 28.015 | 22.852 | 19.011 | 14.705 | 10.814 | 7.365 | 3.523 | 1.492 | 1.125 | 0.832 | 1.468 | 1.982 | 2.055 | 2.642 | 3.474 | 4.38 | 4.893 | 6.386
267 | 49.357 | 46.872 | 47.375 | 45.079 | 41.996 | 39.668 | 36.019 | 29.381 | 24.443 | 18.906 | 13.904 | 9.469 | 4.53 | 1.919 | 1.447 | 1.07 | 1.887 | 2.548 | 2.642 | 3.397 | 4.467 | 5.631 | 6.292 | 8.21
268 | 42.886 | 40.726 | 41.164 | 39.168 | 36.49 | 34.467 | 31.296 | 25.529 | 21.238 | 16.427 | 12.081 | 8.227 | 3.936 | 1.667 | 1.257 | 0.929 | 1.64 | 2.214 | 2.296 | 2.952 | 3.881 | 4.893 | 5.467 | 7.134
273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 35 | 35 | 36 | 37 | 37 | 35 | 31 | 38 | 26 | 20 | 20
273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 38 | 26 | 20 | 20
273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 24 | 27 | 30 | 34 | 34 | 34 | 34 | 36 | 37 | 37 | 35 | 32 | 37 | 25 | 21 | 21
293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Gen Q (Mvar)
bus | t1 | t2 | t3 | t4 | t5 | t6 | t7 | t8 | t9 | t10 | t11 | t12 | t13 | t14 | t15 | t16 | t17 | t18 | t19 | t20 | t21 | t22 | t23 | t24
1 | -14.42 | 5.1443 | 17.2447 | 13.6199 | -13.7366 | -50.4026 | -54.8876 | -44.1573 | -46.6043 | -44.5088 | -44.6479 | -42.3917 | -44.2322 | -43.6667 | -33.9891 | -32.9008 | -44.5772 | -46.5899 | -44.377 | -38.4829 | -40.0058 | -43.0753 | -49.3605 | -4.4531
2 | -87.4324 | -87.8875 | -86.5264 | -85.743 | -81.7545 | -82.6193 | -39.6465 | -20.1354 | -40.4714 | -47.4556 | -49.9418 | -42.3579 | -42.2342 | -39.818 | -41.1105 | -43.1067 | -48.1177 | -10.4748 | -20.134 | -20.7961 | -26.1467 | -34.6929 | -28.9185 | -36.7767
3 | -22.8612 | -22.6433 | -23.8712 | -23.876 | -20.0325 | -23.9266 | -20.201 | -19.6593 | -20.3558 | -20.9965 | -21.4379 | -19.0099 | -19.3285 | -19.5461 | -20.2224 | -19.2675 | -19.6222 | -18.9229 | -17.5287 | -22.4686 | -21.4308 | -19.5376 | -26.0817 | -16.7336
4 | -77.5844 | -54.6895 | -40.1215 | -56.1656 | -78.1539 | -78.023 | -51.6778 | -36.3542 | -35.581 | -39.2723 | -45.9672 | -56.7388 | -57.1413 | -57.3077 | -56.8013 | -56.8915 | -56.4067 | -33.3654 | -37.9673 | -40.0185 | -39.5609 | -45.7548 | -57.1755 | -58.9412
5 | -6.7095 | -2.6201 | 2.0968 | -0.61887 | -5.2558 | -13.938 | -11.5253 | -10.7976 | -9.8776 | -10.4444 | -10.4349 | -9.3629 | -9.4989 | -8.6844 | -7.2224 | -7.5405 | -7.9876 | -9.0756 | -9.1938 | -8.664 | -8.3381 | -8.987 | -13.9927 | -6.5438
6 | -3.5052 | -1.1045 | 2.0869 | 0.61774 | -2.1844 | -7.8329 | -6.0984 | -5.7541 | -5.0017 | -5.3202 | -5.2609 | -4.7972 | -4.5408 | -4.5656 | -3.8955 | -3.7133 | -4.0602 | -4.8578 | -4.8051 | -4.9678 | -4.7263 | -5.5084 | -7.9938 | -4.126
7 | 8.6133 | 7.6034 | 6.4668 | 5.6103 | 4.061 | 6.7255 | 24.6429 | 85.497 | 50.0833 | 38.1327 | 28.5603 | 21.3643 | 20.7491 | 20.15 | 21.4412 | 21.5845 | 22.4661 | 66.3825 | 48.6346 | 36.618 | 35.8451 | 32.6913 | 25.405 | 14.4316
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5908 | 4.2819 | 3.4019 | 2.4206 | 2.2273 | 2.0982 | 2.2886 | 2.3544 | 2.5627 | 6.31 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1843 | 5.7682 | 4.5826 | 3.2607 | 3.0004 | 2.8265 | 3.0829 | 3.1716 | 3.4522 | 8.5002 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91502 | 1.8171 | 1.984 | 2.6045 | 2.0392 | 1.2627 | 1.1671 | 1.1124 | 1.6915 | 1.9711 | 1.7589 | 2.4546 | 2.7641 | 1.5117 | 2.4606 | 2.3194 | -0.56028 | 4.9068
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0.91502 | 1.8171 | 1.984 | 2.6045 | 2.0392 | 1.2627 | 1.1671 | 1.1124 | 1.6915 | 1.9711 | 1.7589 | 2.4546 | 2.7641 | 1.5117 | 2.4606 | 2.3194 | -0.56028 | 4.9068
61 | 0 | 0 | 0 | 0 | 0 | 0 | -0.52407 | -1.244 | -0.69558 | -0.582 | -0.63517 | -0.76844 | -1.2017 | -0.39759 | -0.51807 | -0.51883 | 0.077955 | -0.098395 | -0.41479 | 0.10012 | 0.57959 | 0.24708 | 1.5156 | 0.89126
61 | 0 | 0 | 0 | 0 | 0 | 0 | -0.52407 | -1.244 | -0.69558 | -0.582 | -0.63517 | -0.76844 | -1.2017 | -0.39759 | -0.51807 | -0.51883 | 0.077955 | -0.098395 | -0.41479 | 0.10012 | 0.57959 | 0.24708 | 1.5156 | 0.89126
61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 0.30319 | 0.45057 | 0.31824 | 0.27511 | 0.043028 | 0.096718 | 0.31801 | 0.44512 | 0.53904 | 0.61165 | 0.56117 | 0.461 | 0.42928 | 0.46576 | 0.51092 | 0.49999 | 0.55631 | 0.39188 | 0.50796 | -0.2454 | 0.0082189 | 0.29923 | 1.0257 | 0.41842
108 | 0.50182 | 0.74574 | 0.52673 | 0.45533 | 0.071216 | 0.16008 | 0.52635 | 0.73672 | 0.89217 | 1.0123 | 0.9288 | 0.763 | 0.7105 | 0.77088 | 0.84562 | 0.82753 | 0.92076 | 0.6486 | 0.84074 | -0.40617 | 0.013603 | 0.49527 | 1.6976 | 0.69253
109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7234 | 2.6155 | 2.6749 | 3.2951 | 0 | 0
109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2704 | 5.0616 | 5.1766 | 6.377 | 5.6735 | 0
109 | 1.7278 | -0.026112 | -1.0711 | -1.7601 | -3.9872 | -1.2933 | 2.9623 | 6.0498 | 8.8323 | 9.5112 | 9.5113 | 9.5699 | 9.183 | 8.607 | 8.9899 | 8.8806 | 9.1952 | 9.9394 | 7.2305 | 6.8662 | 7.0668 | 9.1605 | 7.9336 | 5.2264
109 | 1.1173 | -0.016886 | -0.69261 | -1.1382 | -2.5783 | -0.8363 | 1.9156 | 3.9121 | 5.7115 | 6.1505 | 6.1506 | 6.1884 | 5.9383 | 5.5658 | 5.8134 | 5.7427 | 5.9462 | 6.4274 | 4.6756 | 4.4401 | 4.5698 | 5.9237 | 5.1303 | 3.3797
109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51563 | 0.55527 | 0.55528 | 0.55869 | 0.53611 | 0.50248 | 0.52484 | 0.51845 | 0.53682 | 0.58027 | 0 | 0 | 0 | 0 | 0 | 0
110 | -2.4701 | -2.7199 | -2.715 | -2.6286 | -0.53327 | -2.4831 | -2.1115 | -1.9924 | -1.6507 | -1.5351 | -1.5613 | -1.4273 | -1.6506 | -1.69 | -1.5828 | -1.6384 | -1.3758 | -1.4997 | -1.248 | -2.5674 | -0.72968 | 1.5365 | -3.0183 | -2.6684
111 | -0.088154 | -0.064486 | -0.027571 | 0.062426 | -1.0725 | 0.079879 | 0.047295 | -0.093941 | 0.10236 | 0.13759 | 0.031029 | 0.11621 | 0.0097191 | -0.069888 | -0.12562 | -0.13645 | 0.070702 | 0.14559 | -0.062985 | 1.588 | 1.588 | -1.588 | -1.588 | -1.588
112 | -30.7074 | -35.8546 | -42.8206 | -39.4856 | -38.01 | -34.7945 | -36.3744 | -33.3041 | -15.3182 | -5.0803 | -5.8892 | -5.6832 | -8.1466 | -10.4523 | -8.948 | -8.8835 | -6.9701 | -5.5323 | 6.6038 | 18.1294 | 15.8472 | 9.3237 | -3.4691 | -16.8459
112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9185 | -0.63626 | -0.73757 | -0.71177 | -1.0203 | -1.3091 | -1.1207 | -1.1126 | -0.87294 | -0.69287 | 0 | 0 | 0 | 0 | 0 | 0
113 | -0.024873 | -0.014299 | -0.0082578 | -0.040795 | 0.167 | -0.014622 | -0.049037 | 0.002359 | -0.023653 | -0.02808 | -0.021619 | -0.034721 | -0.037198 | -0.041313 | -0.03432 | -0.03146 | -0.023983 | -0.0030877 | 0.0054272 | -0.167 | -0.167 | 0.167 | -0.167 | 0.167
113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
113 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.799 | -2.1358 | -1.6443 | -2.6409 | -2.8293 | -3.1422 | -2.6104 | -2.3929 | -1.8242 | -0.23485 | 0 | 0 | 0 | 0 | 0 | 0
114 | 0.16042 | -0.15976 | -0.40597 | -0.68461 | -0.48763 | -0.44422 | -0.11132 | 0.83427 | 1.6986 | 1.9948 | 2.0651 | 2.3781 | 2.2837 | 1.9613 | 2.2534 | 2.2243 | 2.29 | 2.3549 | 2.447 | 2.4395 | 2.7032 | 2.5399 | 2.2604 | 1.558
114 | 0.73143 | -0.72842 | -1.851 | -3.1214 | -2.2233 | -2.0254 | -0.50753 | 3.8037 | 7.7444 | 9.0949 | 9.4154 | 10.8428 | 10.4123 | 8.9424 | 10.2739 | 10.1415 | 10.4409 | 10.7371 | 11.1568 | 11.1225 | 12.3248 | 11.5803 | 10.3058 | 7.1036
114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
114 | 0.1495 | -0.14889 | -0.37833 | -0.638 | -0.45444 | -0.41398 | -0.10374 | 0.77748 | 1.5829 | 1.859 | 1.9245 | 2.2162 | 2.1283 | 1.8278 | 2.1 | 2.0729 | 2.1341 | 2.1946 | 2.2804 | 2.2734 | 2.5192 | 2.367 | 2.1065 | 1.452
114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.24962 | 0.29314 | 0.30347 | 0.34948 | 0.33561 | 0.28823 | 0.33115 | 0.32688 | 0.33653 | 0.34608 | 0 | 0 | 0 | 0 | 0 | 0
115 | 0 | 0.38949 | 0.58315 | 0.40656 | 0 | 0 | 0 | 0.10334 | 0.21837 | 0.1423 | 0.12245 | 0 | 0 | 0 | 0 | 0.2511 | 0 | 0.35543 | 0.30074 | 0.99022 | -1.2646 | 1.9853 | 0 | 0
115 | 0 | 0.38949 | 0.58315 | 0.40656 | 0 | 0 | 0 | 0 | 0.21837 | 0.1423 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35543 | 0.30074 | 0.99022 | 0 | 0 | 0 | 0
115 | -0.0083444 | -0.013112 | -0.0042183 | -0.012328 | -0.097053 | -0.020512 | -0.024721 | -0.026254 | -0.020971 | -0.024465 | -0.025376 | 0.0028446 | -0.022564 | -0.012882 | -0.016783 | -0.019468 | -0.0046933 | -0.014677 | -0.017188 | 0.014477 | -0.089078 | 0.060179 | -0.1976 | 0.011351
115 | -0.069148 | -0.10866 | -0.034956 | -0.10216 | -0.80425 | -0.16998 | -0.20485 | -0.21756 | -0.17378 | -0.20273 | -0.21029 | 0.023572 | -0.18698 | -0.10675 | -0.13908 | -0.16133 | -0.038892 | -0.12162 | -0.14244 | 0.11997 | -0.73816 | 0.49869 | -1.6375 | 0.094061
115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | -0.18498 | -1.5994 | -0.29751 | -2.5203 | -2.6043 | -0.94952 | -1.8277 | -0.66784 | 0.17256 | 2.0967 | 2.2901 | 1.8268 | 0.77169 | 0.96346 | 2.0637 | 1.8673 | 1.4656 | 1.9156 | 3.5014 | 1.9482 | 8.8536 | 7.8803 | 2.5617 | 1.3695
116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0050301 | 0.061118 | 0.066757 | 0.053251 | 0.022495 | 0.028085 | 0.060157 | 0.054432 | 0.042722 | 0.05584 | 0 | 0 | 0 | 0 | 0 | 0
117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0011151 | 0.32714 | 0.36047 | 0.26875 | 0.16436 | 0.2112 | 0.21047 | 0.18822 | 0.29901 | 0.32945 | 0 | 0 | 0 | 0 | 0 | 0
118 | 2.802 | 2.4699 | 2.0952 | 1.7872 | 2.0036 | 1.6485 | 1.9237 | 2.6408 | 3.0724 | 3.2097 | 3.0897 | 3.3554 | 3.1405 | 3.3828 | 3.6028 | 3.6041 | 3.3123 | 3.3304 | 3.533 | 3.3344 | 3.6421 | 3.7784 | 4.0208 | 2.5965
118 | 0.094094 | 0.082939 | 0.070357 | 0.060017 | 0.067282 | 0.055357 | 0.064601 | 0.088681 | 0.10317 | 0.10779 | 0.10375 | 0.11268 | 0.10546 | 0.1136 | 0.12099 | 0.12103 | 0.11123 | 0.11184 | 0.11864 | 0.11197 | 0.1223 | 0.12688 | 0.13502 | 0.087192
118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 | 5.6836 | 5.0098 | 4.2498 | 3.6252 | 4.0641 | 3.3437 | 3.9021 | 5.3566 | 6.232 | 6.5106 | 6.2671 | 6.806 | 6.3701 | 6.8616 | 7.3079 | 7.3105 | 6.7185 | 6.7553 | 7.1663 | 6.7634 | 7.3876 | 7.6641 | 8.1557 | 5.2667
119 | -0.82189 | -0.88058 | -0.91753 | -0.88529 | -0.77515 | -0.85838 | -0.8321 | -0.70068 | -0.47826 | -0.434 | -0.42372 | -0.43018 | -0.45575 | -0.50388 | -0.48715 | -0.47147 | -0.44249 | -0.30103 | -0.14551 | -0.4506 | -0.60624 | -0.39643 | -0.45844 | -0.57659
119 | -5.7549 | -6.1659 | -6.4246 | -6.1989 | -5.4277 | -6.0105 | -5.8264 | -4.9062 | -3.3488 | -3.0389 | -2.9669 | -3.0122 | -3.1912 | -3.5282 | -3.411 | -3.3013 | -3.0983 | -2.1078 | -1.0189 | -3.1551 | -4.2449 | -2.7758 | -3.21 | -4.0373
119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.18397 | -0.16695 | -0.16299 | -0.16548 | -0.17531 | -0.19383 | -0.18739 | -0.18136 | -0.17021 | -0.1158 | 0 | 0 | 0 | 0 | 0 | 0
120 | 0.28717 | 0.17686 | -0.13656 | -0.12312 | 0.50388 | -0.11477 | 0.26648 | 0.62178 | 1.3106 | 1.6127 | 1.6711 | 1.7542 | 1.7282 | 1.8547 | 2.1409 | 2.0503 | 2.1569 | 1.4881 | 1.8119 | 2.6838 | 2.58 | 0.82133 | 1.2854 | 0.91798
120 | 0.45842 | 0.28233 | -0.218 | -0.19654 | 0.80436 | -0.18322 | 0.42539 | 0.99257 | 2.0922 | 2.5744 | 2.6677 | 2.8002 | 2.7588 | 2.9607 | 3.4175 | 3.2729 | 3.4431 | 2.3755 | 2.8924 | 4.2843 | 4.1186 | 1.3111 | 2.0519 | 1.4654
120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20976 | 0.25811 | 0.26746 | 0.28076 | 0.2766 | 0.29685 | 0.34265 | 0.32815 | 0.34521 | 0.23818 | 0 | 0 | 0 | 0 | 0 | 0
121 | 0.1061 | 0.084105 | 0.18761 | 0.15882 | 1.811 | 0.10135 | 0.15177 | 0.45969 | 0.85909 | 0.74409 | 0.73505 | 0.66638 | 0.65347 | 0.65001 | 0.67933 | 0.68494 | 0.67795 | 0.92557 | 0.51626 | -0.053271 | -0.085129 | -1.0142 | -0.30491 | 1.811
121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6427 | 2.289 | 2.2612 | 2.0499 | 2.0102 | 1.9996 | 2.0898 | 2.107 | 2.0855 | 2.8472 | 0 | 0 | 0 | 0 | 0 | 0
122 | -2.8969 | -3.3671 | -3.4851 | -3.5585 | -3.6667 | -3.0062 | -2.9217 | -1.264 | 0.0030253 | -0.021318 | 0.29011 | -0.058273 | -0.28706 | -0.77664 | -0.45369 | -0.43067 | 0.19388 | 0.86809 | 0.84666 | 0.4977 | 0.35505 | 1.642 | 0.74351 | -2.1292
122 | -19.5165 | -22.6841 | -23.4791 | -23.9742 | -24.7029 | -20.2528 | -19.6835 | -8.5154 | 0.020382 | -0.14362 | 1.9545 | -0.39259 | -1.9339 | -5.2323 | -3.0565 | -2.9014 | 1.3062 | 5.8484 | 5.704 | 3.353 | 2.392 | 11.0623 | 5.0091 | -14.3447
122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4278e-05 | -0.00010061 | 0.0013691 | -0.00027501 | -0.0013547 | -0.0036652 | -0.0021411 | -0.0020325 | 0.00091498 | 0.0040969 | 0 | 0 | 0 | 0 | 0 | 0
123 | -5.9523 | -6.5842 | -7.2795 | -6.8031 | -10.6167 | -6.2562 | -5.9525 | -5.0386 | -0.99629 | 0.093159 | -0.14018 | -0.049061 | -0.81433 | -1.2189 | -1.0406 | -0.89429 | -0.58995 | 1.2212 | 2.6531 | 6.1555 | 5.2342 | 2.6855 | 2.2567 | -3.2871
123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.42633 | 0.039864 | -0.059984 | -0.020994 | -0.34846 | -0.5216 | -0.44527 | -0.38268 | -0.25245 | 0.52257 | 0 | 0 | 0 | 0 | 0 | 0
124 | -0.0032478 | -0.0064166 | -0.0088343 | -0.0094142 | -0.0087504 | -0.0065962 | -5.9175e-05 | 0.0072843 | 0.013948 | 0.013763 | 0.014579 | 0.015026 | 0.01419 | 0.010888 | 0.013751 | 0.013738 | 0.014548 | 0.018097 | 0.017119 | 0.016398 | 0.01623 | 0.021864 | 0.016686 | 0.0076777
124 | -7.0564 | -13.9409 | -19.1938 | -20.4536 | -19.0115 | -14.3312 | -0.12857 | 15.8262 | 30.304 | 29.9029 | 31.676 | 32.647 | 30.8293 | 23.6567 | 29.8762 | 29.8469 | 31.6074 | 39.3186 | 37.1926 | 35.6266 | 35.2618 | 47.5021 | 36.2519 | 16.6809
124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
125 | -1.2066 | -1.4638 | -1.5765 | -1.797 | -0.36665 | -1.4412 | 0.14194 | 0.16241 | 0.037361 | 0.15234 | 0.28594 | 0.13799 | 0.38982 | 0.19732 | 0.13799 | 0.020654 | 0.38618 | 0.24027 | 0.21664 | -1.4949 | -1.4473 | 1.2586 | -2.4947 | -0.81334
126 | -0.50217 | -0.38232 | -0.28245 | -0.78759 | -3.4183 | -0.65803 | -1.0606 | 0.024454 | 0.059279 | 0.019636 | -0.099711 | -0.38804 | -0.25481 | -0.41912 | -0.27661 | -0.45561 | -0.31473 | 0.33896 | 0.35006 | 0.71235 | 0.49194 | 0.7317 | 0.67082 | 0.75973
126 | -0.28393 | -0.21617 | -0.1597 | -0.4453 | -1.9327 | -0.37205 | -0.59967 | 0.013826 | 0.033517 | 0.011102 | -0.056377 | -0.2194 | -0.14407 | -0.23697 | -0.1564 | -0.2576 | -0.17795 | 0.19165 | 0.19792 | 0.40276 | 0.27815 | 0.4137 | 0.37928 | 0.42955
126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.030713 | 0.010173 | -0.05166 | -0.20104 | -0.13202 | -0.21715 | -0.14331 | -0.23605 | -0.16306 | 0.17562 | 0 | 0 | 0 | 0 | 0 | 0
127 | -0.0096097 | -0.013292 | -0.0148 | -0.016066 | -0.026963 | -0.019194 | -0.013558 | -0.0073727 | -0.0036859 | -0.0022707 | -0.0029248 | -0.0053157 | -0.0049837 | -0.006691 | -0.0062521 | -0.0056704 | -0.00072917 | 0.00039318 | 0.0035515 | 0.0023072 | -0.0030499 | -0.011991 | -0.008157 | -0.014148
127 | -3.613 | -4.9974 | -5.5646 | -6.0405 | -10.1374 | -7.2164 | -5.0975 | -2.772 | -1.3858 | -0.85374 | -1.0997 | -1.9986 | -1.8738 | -2.5157 | -2.3506 | -2.1319 | -0.27415 | 0.14782 | 1.3353 | 0.86746 | -1.1467 | -4.5085 | -3.0668 | -5.3192
127 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
127 | -0.31781 | -0.43958 | -0.48948 | -0.53134 | -0.89171 | -0.63477 | -0.44839 | -0.24383 | -0.1219 | -0.075097 | -0.096728 | -0.1758 | -0.16482 | -0.22128 | -0.20677 | -0.18753 | -0.024115 | 0.013003 | 0.11746 | 0.076304 | -0.10087 | -0.39658 | -0.26977 | -0.46789
128 | 16.1964 | 13.5424 | 13.0023 | 15.6406 | 16.6288 | 9.4701 | 10.3738 | 17.0211 | 19.1184 | 20.9761 | 22.1352 | 22.326 | 21.1641 | 21.1186 | 24.0101 | 23.719 | 23.978 | 25.9218 | 28.2877 | 32.4022 | 29.3089 | 24.3057 | 27.6834 | 22.1832
128 | 0.22057 | 0.18442 | 0.17707 | 0.213 | 0.22646 | 0.12897 | 0.14127 | 0.2318 | 0.26036 | 0.28566 | 0.30144 | 0.30404 | 0.28822 | 0.2876 | 0.32698 | 0.32301 | 0.32654 | 0.35301 | 0.38523 | 0.44126 | 0.39914 | 0.331 | 0.377 | 0.3021
128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3075 | 0.33738 | 0.35603 | 0.3591 | 0.34041 | 0.33968 | 0.38618 | 0.3815 | 0.38567 | 0.41693 | 0 | 0 | 0 | 0 | 0 | 0
129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.553 | 13.3777 | 14.7459 | 15.1619 | 16.0072 | 15.6467 | 0 | 0 | 0 | 0 | 14.1013 | 15.2587 | 15.5037 | 14.9825 | 17.8455 | 0 | 0
129 | 7.4811 | 5.9953 | 4.9981 | 4.7001 | 4.4645 | 5.6538 | 6.8614 | 6.0731 | 8.2893 | 9.3629 | 9.6893 | 10.3525 | 10.0696 | 12.1979 | 12.7242 | 12.593 | 12.6874 | 8.8571 | 9.7652 | 9.9574 | 9.5485 | 11.7948 | 12.5462 | 10.9125
129 | 3.6094 | 2.8926 | 2.4115 | 2.2677 | 2.154 | 2.7278 | 3.3105 | 2.9301 | 3.9994 | 4.5174 | 4.6748 | 4.9948 | 4.8584 | 5.8852 | 6.1392 | 6.0758 | 6.1214 | 4.2733 | 4.7115 | 4.8042 | 4.6069 | 5.6907 | 6.0532 | 5.265
129 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
130 | 0.21045 | 0.3555 | -0.14819 | 0.00047677 | 0.18244 | 0.092648 | 0.055458 | 0.11152 | 0.12012 | 0.073963 | -0.10675 | 0.29235 | -0.066664 | -0.21565 | 0.29792 | 0.17641 | 0.045088 | 0.35345 | -0.19531 | 2.395 | 1.2792 | 1.5707 | 2.3413 | 1.9376
131 | -17.4448 | -18.0577 | -18.4942 | -18.4782 | -17.6219 | -17.4674 | -17.3117 | -16.2077 | -11.5921 | -10.3539 | -9.9128 | -10.0475 | -10.8232 | -11.5586 | -11.3505 | -11.3716 | -10.5347 | -7.4758 | -4.7934 | -5.2287 | -7.5999 | -4.8828 | -9.2986 | -13.7526
131 | -12.1533 | -12.5802 | -12.8844 | -12.8732 | -12.2767 | -12.169 | -12.0605 | -11.2914 | -8.0759 | -7.2133 | -6.9059 | -6.9998 | -7.5402 | -8.0525 | -7.9075 | -7.9222 | -7.3392 | -5.2082 | -3.3394 | -3.6427 | -5.2946 | -3.4017 | -6.478 | -9.581
131 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -2.5133 | -2.2448 | -2.1492 | -2.1784 | -2.3466 | -2.506 | -2.4609 | -2.4655 | -2.284 | -1.6208 | 0 | 0 | 0 | 0 | 0 | 0
132 | -1.6527 | -2.245 | -2.1534 | -1.8065 | -1.2827 | -1.6108 | -1.4162 | -1.1691 | -0.53084 | -0.5723 | -0.39665 | -0.40564 | -0.44178 | -1.0616 | -0.74459 | -0.65116 | -0.49709 | -0.11146 | -0.42408 | -0.39682 | 0.044972 | 0.32075 | 0.6922 | -1.43
132 | -1.0703 | -1.4538 | -1.3945 | -1.1699 | -0.8307 | -1.0432 | -0.9171 | -0.7571 | -0.34377 | -0.37062 | -0.25687 | -0.2627 | -0.2861 | -0.6875 | -0.4822 | -0.42169 | -0.32192 | -0.072179 | -0.27464 | -0.25698 | 0.029124 | 0.20772 | 0.44827 | -0.92604
133 | 2.8247 | 2.5015 | 1.8779 | 1.6255 | 0.91393 | 1.1859 | 1.2294 | 3.0577 | 4.9174 | 6.1653 | 6.1745 | 5.9905 | 5.705 | 5.6138 | 6.2547 | 6.1147 | 5.9834 | 6.144 | 7.5779 | 7.1143 | 7.823 | 7.9526 | 6.0218 | 5.2373
133 | 2.5899 | 2.2935 | 1.7217 | 1.4904 | 0.83795 | 1.0873 | 1.1272 | 2.8035 | 4.5085 | 5.6528 | 5.6612 | 5.4925 | 5.2307 | 5.147 | 5.7347 | 5.6063 | 5.4859 | 5.6332 | 6.9479 | 6.5228 | 7.1726 | 7.2914 | 5.5212 | 4.8019
133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
134 | 2.2562 | -1.4002 | -1.2131 | -2.6116 | -3.3465 | -4.2213 | -1.9945 | 1.7881 | 6.8907 | 7.5449 | 7.9459 | 9.2241 | 8.0533 | 7.1858 | 7.9766 | 7.6244 | 7.3711 | 10.5031 | 16.0579 | 13.0588 | 11.0095 | 8.8399 | 9.1285 | 5.4225
134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.044518 | 0.048745 | 0.051335 | 0.059593 | 0.052029 | 0.046424 | 0.051534 | 0.049258 | 0.047622 | 0.067857 | 0 | 0 | 0 | 0 | 0 | 0
136 | -0.50464 | -0.34684 | -0.42443 | -0.49087 | -1.504 | -0.3837 | -0.40104 | -0.30577 | -0.1959 | -0.27662 | -0.19523 | -0.19174 | -0.1041 | -0.25029 | -0.26453 | -0.27421 | -0.23168 | -0.0856 | -0.11178 | -1.504 | -0.62131 | -1.504 | 0.46583 | 1.504
136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.1451 | -0.20489 | -0.1446 | -0.14202 | -0.07711 | -0.18538 | -0.19593 | -0.20311 | -0.1716 | -0.063403 | 0 | 0 | 0 | 0 | 0 | 0
137 | 2.7545 | 2.5523 | 2.6563 | 2.5515 | 2.4441 | 2.4962 | 2.4804 | 2.8625 | 3.1386 | 3.2159 | 3.2476 | 3.2694 | 3.2092 | 3.0991 | 3.2939 | 3.2492 | 3.3281 | 3.342 | 3.4426 | 4.0105 | 3.2957 | 1.9298 | 4.7452 | 4.6058
137 | 4.2196 | 3.9098 | 4.0691 | 3.9086 | 3.7441 | 3.824 | 3.7996 | 4.3851 | 4.808 | 4.9264 | 4.975 | 5.0083 | 4.9162 | 4.7475 | 5.0458 | 4.9775 | 5.0983 | 5.1196 | 5.2736 | 6.1437 | 5.0487 | 2.9562 | 7.2691 | 7.0556
137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | -0.11515 | -0.067987 | -0.097885 | 0.21991 | 1.504 | -0.084656 | -0.28842 | -0.0015688 | -0.13191 | 0.023112 | -0.16714 | 0.18469 | -0.047194 | -0.059767 | 0.10857 | 0.013491 | -0.032979 | -0.071305 | 0.19359 | -1.504 | 1.504 | 1.1788 | 1.504 | -1.504
138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.14174 | 0.024833 | -0.17959 | 0.19845 | -0.050708 | -0.064217 | 0.11666 | 0.014495 | -0.035435 | -0.076615 | 0 | 0 | 0 | 0 | 0 | 0
139 | -0.84013 | -0.74254 | -0.94436 | -0.88585 | -0.59394 | -0.91128 | -0.85407 | -0.48551 | -0.53623 | -0.31284 | -0.36976 | -0.48671 | -0.2629 | -0.52631 | -0.57176 | -0.45796 | -0.48537 | -0.1209 | -0.17424 | 0.91389 | 2.423 | 0.18216 | -2.423 | 0.90411
140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1998 | 6.0153 | 5.3831 | 4.7122 | 4.3468 | 3.7474 | 5.047 | 5.7829 | 6.9904 | 8.6321 | 0 | 0 | 0 | 0 | 0 | 0
141 | -0.20475 | -0.3479 | -0.46761 | -0.45698 | 3.1601 | -0.34614 | -0.22403 | 0.022079 | 0.4401 | 0.57261 | 0.68283 | 0.58665 | 0.64553 | 0.50843 | 0.5653 | 0.42161 | 0.63734 | 0.74201 | 0.94007 | 0.24418 | -0.16517 | 3.398 | 0.11742 | -1.5802
142 | 1.0134 | 0.78752 | 0.93716 | 0.79207 | 0.88204 | 0.71821 | 0.9861 | 1.4539 | 1.8225 | 2.0397 | 2.1019 | 2.0467 | 1.9923 | 1.9819 | 2.0719 | 2.0251 | 2.0817 | 2.2936 | 2.5749 | 2.056 | 2.0398 | 1.9725 | 1.8578 | 1.4584
142 | 6.0747 | 4.7208 | 5.6177 | 4.748 | 5.2874 | 4.3053 | 5.9111 | 8.7155 | 10.9248 | 12.2267 | 12.5999 | 12.2689 | 11.9429 | 11.8803 | 12.4198 | 12.1393 | 12.4785 | 13.7487 | 15.435 | 12.3246 | 12.2272 | 11.824 | 11.1362 | 8.7423
142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
142 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0097964 | 0.010964 | 0.011299 | 0.011002 | 0.010709 | 0.010653 | 0.011137 | 0.010886 | 0.01119 | 0.012329 | 0 | 0 | 0 | 0 | 0 | 0
144 | -0.0032971 | -0.011824 | -0.015079 | -0.01691 | -0.032986 | -0.013209 | -0.0056785 | 0.0029591 | 0.012603 | 0.018818 | 0.018473 | 0.020124 | 0.018988 | 0.021671 | 0.024664 | 0.02733 | 0.030544 | 0.021392 | 0.030365 | 0.014478 | -0.0009482 | 0.011704 | 0.023886 | 0.0055827
144 | -0.36242 | -1.2998 | -1.6575 | -1.8588 | -3.6258 | -1.452 | -0.62419 | 0.32527 | 1.3853 | 2.0685 | 2.0306 | 2.212 | 2.0872 | 2.382 | 2.7111 | 3.0041 | 3.3574 | 2.3515 | 3.3378 | 1.5914 | -0.10423 | 1.2865 | 2.6256 | 0.61366
145 | -28.0911 | -32.2686 | -34.0085 | -37.651 | -34.1378 | -29.3662 | -29.0489 | -6.8955 | -2.2186 | -1.9465 | 0.027386 | 0.1944 | -0.84601 | -2.1016 | -2.0746 | -1.7599 | 0.14228 | 1.2207 | 1.3809 | 8.2479 | 10.9439 | 20.4649 | 14.8956 | -15.3488
145 | -0.57829 | -0.66428 | -0.7001 | -0.77508 | -0.70276 | -0.60453 | -0.598 | -0.14195 | -0.045673 | -0.040071 | 0.00056377 | 0.0040019 | -0.017416 | -0.043263 | -0.042707 | -0.03623 | 0.002929 | 0.025129 | 0.028427 | 0.16979 | 0.22529 | 0.42129 | 0.30664 | -0.31597
146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4234 | 0.38098 | 0.34217 | 0.23923 | 0.19523 | 0.2498 | 0.20271 | 0.21134 | 0.24707 | 0.65125 | 0 | 0 | 0 | 0 | 0 | 0
147 | -0.10262 | -0.088589 | -0.21037 | -0.22456 | 0.15042 | -0.14263 | -0.11876 | -0.17667 | -0.057976 | -0.048422 | -0.052157 | -0.026746 | -0.026494 | -0.027947 | -0.070634 | -0.046404 | -0.021327 | -0.043254 | -0.047154 | 0.098931 | -0.43973 | -1.365 | 0.63654 | -1.365
147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.047315 | -0.039518 | -0.042567 | -0.021828 | -0.021623 | -0.022808 | -0.057646 | -0.037871 | -0.017406 | -0.0353 | 0 | 0 | 0 | 0 | 0 | 0
149 | 0.010222 | 0.055624 | 0.016504 | 0.0063311 | -0.306 | 0.021641 | 0.10195 | -0.012178 | 0.14406 | 0.12942 | 0.13358 | 0.11885 | 0.11731 | 0.11883 | 0.11064 | 0.12047 | 0.12295 | 0.15664 | -0.021671 | 0.306 | 0.306 | 0.306 | 0.10983 | -0.306
149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7048 | 1.5314 | 1.5807 | 1.4064 | 1.3882 | 1.4062 | 1.3092 | 1.4256 | 1.4549 | 1.8536 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0.58614 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8466 | 0.82493 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8466 | 0.82493 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 1.8777 | 1.2635 | 1.4665 | 1.3355 | 0.6781 | 1.5346 | 1.998 | 2.4297 | 2.2271 | 2.6862 | 2.7639 | 2.6108 | 2.7656 | 2.6158 | 2.6332 | 2.4601 | 2.6659 | 3.0276 | 2.5484 | 2.4415 | 3.9643 | 3.1109 | 2.3409 | 1.7729
150 | 2.1884 | 1.4726 | 1.7092 | 1.5565 | 0.79029 | 1.7885 | 2.3286 | 2.8317 | 2.5956 | 3.1307 | 3.2212 | 3.0428 | 3.2231 | 3.0486 | 3.0689 | 2.8671 | 3.107 | 3.5285 | 2.97 | 2.8454 | 4.6202 | 3.6256 | 2.7282 | 2.0662
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0162 | 1.2257 | 1.2611 | 1.1913 | 1.2619 | 1.1936 | 1.2015 | 1.1225 | 1.2164 | 1.3815 | 0 | 0 | 0 | 0 | 0 | 0
151 | 2.4153 | 2.2891 | 2.0278 | 1.9589 | 4.282 | 1.6886 | 2.4076 | 2.6513 | 3.2694 | 3.4955 | 3.3961 | 3.425 | 3.2919 | 3.3299 | 3.403 | 3.3419 | 3.3775 | 3.2406 | 3.5345 | 0.56198 | 1.5291 | 3.4283 | 4.7546 | 4.4706
151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152 | 0.30052 | 0.23167 | 0.1839 | 0.18417 | 0.23023 | 0.31116 | 0.36146 | 0.42281 | 0.53949 | 0.71016 | 0.77603 | 0.78805 | 0.83832 | 0.77956 | 0.79529 | 0.70678 | 0.78016 | 0.81937 | 0.8533 | 0.87134 | 0.90278 | 1.2436 | 1.0487 | 0.77792
152 | 1.1432 | 0.88126 | 0.69955 | 0.70057 | 0.87577 | 1.1836 | 1.3749 | 1.6083 | 2.0522 | 2.7014 | 2.9519 | 2.9977 | 3.1889 | 2.9654 | 3.0252 | 2.6885 | 2.9676 | 3.1168 | 3.2458 | 3.3145 | 3.4341 | 4.7304 | 3.989 | 2.9591
152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
152 | 0.37711 | 0.29071 | 0.23077 | 0.2311 | 0.2889 | 0.39045 | 0.45356 | 0.53055 | 0.67697 | 0.89113 | 0.97378 | 0.98887 | 1.0519 | 0.97821 | 0.99795 | 0.88689 | 0.97896 | 1.0282 | 1.0707 | 1.0934 | 1.1328 | 1.5605 | 1.3159 | 0.97616
152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0021267 | 0.0027995 | 0.0030591 | 0.0031065 | 0.0033047 | 0.003073 | 0.003135 | 0.0027861 | 0.0030754 | 0.00323 | 0 | 0 | 0 | 0 | 0 | 0
153 | -0.10794 | -0.071167 | -0.10351 | -0.13008 | -0.8392 | -0.13302 | 0.025465 | -0.010026 | -0.066802 | -0.040033 | -0.0063867 | -0.054175 | -0.024635 | -0.011348 | 0.026838 | -0.081208 | -0.032221 | -0.039625 | -0.036041 | -1.198 | -1.198 | -0.072937 | -0.087654 | -1.198
153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.0015613 | -0.00093567 | -0.00014927 | -0.0012662 | -0.00057577 | -0.00026523 | 0.00062726 | -0.001898 | -0.00075309 | -0.00092613 | 0 | 0 | 0 | 0 | 0 | 0
154 | -0.041317 | -0.019581 | -0.12698 | -0.02136 | 1.142 | -0.11069 | 0.10645 | 0.12767 | 0.051089 | 0.014125 | 0.0055309 | 0.044089 | -0.0037458 | 0.057843 | -0.053444 | -0.020519 | 0.086411 | 0.075051 | 0.002647 | 1.142 | 1.142 | 1.142 | -0.09078 | -1.142
154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.021205 | 0.0058628 | 0.0022957 | 0.0183 | -0.0015548 | 0.024009 | -0.022182 | -0.0085165 | 0.035866 | 0.031151 | 0 | 0 | 0 | 0 | 0 | 0
155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
155 | -0.0050932 | -0.0055584 | -0.0081806 | -0.010468 | -0.015917 | -0.013391 | -0.011596 | -0.0067033 | -0.0034154 | -0.0032699 | -0.004233 | -0.0021219 | -0.0027168 | 0.0025582 | 0.0048639 | 0.0052998 | 0.0027842 | 0.0016601 | 0.0019593 | 0.01064 | 0.01567 | 0.018889 | 0.025012 | 0.014947
155 | -4.359 | -4.7572 | -7.0015 | -8.9594 | -13.6227 | -11.4611 | -9.9249 | -5.7371 | -2.9231 | -2.7985 | -3.6228 | -1.816 | -2.3252 | 2.1894 | 4.1628 | 4.5359 | 2.3829 | 1.4208 | 1.6769 | 9.1067 | 13.4116 | 16.1664 | 21.4069 | 12.7929
155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
156 | -7.8271 | -8.914 | -10.3636 | -10.1653 | -9.7679 | -10.9802 | -7.9855 | -7.2727 | -4.967 | -4.1025 | -3.7344 | -2.3196 | -2.4179 | -1.9483 | -1.0281 | -1.0327 | -0.6139 | -3.5665 | -2.1369 | -3.7857 | -4.8472 | -2.1139 | -3.6374 | -1.5163
156 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
157 | -0.059998 | -0.15762 | -0.31467 | -0.23297 | 1.3878 | -0.26617 | -0.23729 | -0.23926 | -0.087998 | 0.090809 | -0.034514 | 0.073127 | -0.045573 | 0.016191 | 0.017874 | -0.0037324 | -0.020917 | 0.054812 | 0.19227 | -1.2718 | -2.3687 | 2.0394 | 3.1165 | 3.2854
158 | 0.10326 | 0.054947 | 0.047974 | 0.040537 | -0.11853 | 0.0701 | 0.079395 | 0.18315 | 0.2496 | 0.25135 | 0.28295 | 0.27869 | 0.27477 | 0.26987 | 0.30198 | 0.29925 | 0.33421 | 0.30665 | 0.3017 | 0.26511 | 0.22818 | 0.54244 | 0.51581 | 0.12874
158 | 2.3084 | 1.2284 | 1.0725 | 0.90622 | -2.6496 | 1.5671 | 1.7749 | 4.0944 | 5.5798 | 5.619 | 6.3254 | 6.23 | 6.1426 | 6.033 | 6.7508 | 6.6897 | 7.4714 | 6.8552 | 6.7445 | 5.9265 | 5.101 | 12.1262 | 11.5311 | 2.878
159 | 1.3447 | 1.1541 | 1.2904 | 1.25 | 1.1138 | 1.2431 | 1.467 | 1.7618 | 1.6648 | 1.6093 | 1.5655 | 1.5468 | 1.5382 | 1.5026 | 1.5442 | 1.5425 | 1.556 | 1.7225 | 1.7404 | 1.569 | 1.558 | 1.5177 | 1.5368 | 1.3698
159 | 31.7377 | 27.2388 | 30.4558 | 29.5026 | 26.288 | 29.3387 | 34.6233 | 41.5819 | 39.2908 | 37.9829 | 36.9473 | 36.5069 | 36.3033 | 35.4643 | 36.4465 | 36.4055 | 36.7233 | 40.6531 | 41.0754 | 37.0321 | 36.7719 | 35.8192 | 36.2717 | 32.3306
159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
159 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0318 | 0.9975 | 0.9703 | 0.95873 | 0.95339 | 0.93135 | 0.95715 | 0.95607 | 0.96442 | 1.0676 | 0 | 0 | 0 | 0 | 0 | 0
160 | -0.92768 | -1.1589 | -1.1607 | -1.2487 | -1.6352 | -1.1092 | -1.0132 | -0.57545 | -0.13498 | 0.057754 | 0.35095 | 0.65551 | 0.62865 | 0.49049 | 0.89048 | 0.77574 | 1.1225 | 0.54362 | 1.0536 | 1.1585 | 1.0361 | 2.0429 | 2.1107 | 0.6425
160 | -6.8003 | -8.4953 | -8.5083 | -9.1536 | -11.9865 | -8.1311 | -7.4275 | -4.2183 | -0.98947 | 0.42336 | 2.5726 | 4.8052 | 4.6083 | 3.5955 | 6.5276 | 5.6866 | 8.2286 | 3.985 | 7.7235 | 8.4922 | 7.5954 | 14.9753 | 15.4722 | 4.7098
160 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
161 | -3.8677 | -5.3362 | -6.3177 | -8.0763 | -8.3795 | -8.2814 | -5.1037 | 0.51326 | 6.3189 | 7.4471 | 7.042 | 7.0161 | 6.0383 | 4.0527 | 6.093 | 5.9067 | 7.4346 | 10.5077 | 7.1705 | 8.8216 | 9.2102 | 12.13 | 12.6431 | 0.741
162 | 7.7509 | 7.6647 | 7.6064 | 7.4869 | 6.5219 | 7.4357 | 7.7493 | 7.9672 | 8.061 | 8.3843 | 8.5009 | 8.549 | 8.657 | 8.4953 | 8.4223 | 8.403 | 8.4871 | 8.5535 | 8.5588 | 8.7553 | 8.6606 | 8.2414 | 8.0318 | 6.7122
162 | 5.5854 | 5.5232 | 5.4813 | 5.3952 | 4.6997 | 5.3583 | 5.5843 | 5.7413 | 5.8088 | 6.0418 | 6.1258 | 6.1605 | 6.2383 | 6.1218 | 6.0692 | 6.0553 | 6.1159 | 6.1637 | 6.1676 | 6.3092 | 6.241 | 5.9389 | 5.7878 | 4.8369
162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
163 | -1.9391 | -0.79812 | -1.6186 | -2.1545 | -4.7819 | -4.4971 | -1.928 | -1.5766 | -1.4767 | -1.166 | -1.5474 | -2.4736 | -2.6675 | -2.166 | -1.5153 | -1.5424 | -1.6822 | -2.4223 | -1.8808 | -2.6335 | -1.0672 | -7.0464 | 0.017837 | -3.5938
163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.9851 | -2.103 | -3.4676 | -5.0201 | -5.099 | -5.1846 | -5.049 | -5.0049 | -4.9017 | -1.617 | 0 | 0 | 0 | 0 | 0 | 0
165 | -8.2466 | -7.8646 | -8.0975 | -6.7567 | -6.0818 | -7.2285 | -5.5121 | -4.7125 | -5.4177 | -5.0918 | -4.7433 | -4.691 | -4.3707 | -4.6068 | -4.8972 | -4.8956 | -5.1517 | -4.0346 | -2.9268 | -2.0892 | -5.6344 | -3.7321 | -1.4811 | -2.9369
165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
166 | -1.2707 | -1.5338 | -1.6469 | -1.6802 | -1.7484 | -1.5518 | -1.1745 | -0.56193 | 0.05874 | 0.22451 | 0.3354 | 0.38968 | 0.32672 | 0.15093 | 0.29147 | 0.30438 | 0.37336 | 0.65826 | 0.92391 | 0.76235 | 0.75073 | 1.1614 | 0.65349 | -0.5805
166 | -15.5882 | -18.8165 | -20.2032 | -20.6117 | -21.4482 | -19.0373 | -14.4076 | -6.8934 | 0.7206 | 2.7542 | 4.1145 | 4.7804 | 4.008 | 1.8515 | 3.5756 | 3.734 | 4.5802 | 8.0752 | 11.334 | 9.3521 | 9.2096 | 14.2469 | 8.0167 | -7.1213
166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00061832 | 0.0023633 | 0.0035305 | 0.0041019 | 0.0034392 | 0.0015887 | 0.0030681 | 0.003204 | 0.0039301 | 0.006929 | 0 | 0 | 0 | 0 | 0 | 0
167 | -0.040804 | -0.041204 | -0.041808 | -0.035377 | -0.022493 | -0.028479 | -0.03824 | -0.052494 | -0.049138 | -0.049381 | -0.041237 | -0.040606 | -0.040466 | -0.049584 | -0.041539 | -0.042141 | -0.042422 | -0.03957 | -0.036036 | -0.010849 | -0.019904 | -0.047906 | -0.032305 | -0.060519
167 | -5.2706 | -5.3224 | -5.4004 | -4.5697 | -2.9054 | -3.6787 | -4.9395 | -6.7808 | -6.3472 | -6.3786 | -5.3267 | -5.2451 | -5.2271 | -6.4049 | -5.3657 | -5.4434 | -5.4797 | -5.1114 | -4.6548 | -1.4014 | -2.571 | -6.1881 | -4.1728 | -7.8173
167 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
168 | -0.25278 | -0.2843 | -0.097863 | -0.61993 | 1.281 | -0.004125 | -0.17874 | -0.25713 | -0.11995 | 0.10444 | 0.028019 | -0.090883 | -0.29111 | -0.28112 | -0.49761 | -0.36722 | -0.12024 | -0.25364 | -0.19792 | -1.281 | 1.281 | -1.281 | 1.281 | -1.281
169 | 25.4114 | 25.2758 | 24.1965 | 23.2375 | 24.3114 | 22.9625 | 29.8452 | 36.7632 | 33.4439 | 32.3208 | 31.2293 | 29.2757 | 28.8491 | 30.0864 | 28.9531 | 28.9588 | 29.2413 | 34.8709 | 35.4826 | 33.4463 | 33.3084 | 33.0779 | 31.776 | 32.6863
169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4461 | 1.3976 | 1.3504 | 1.2659 | 1.2475 | 1.301 | 1.252 | 1.2522 | 1.2644 | 1.5079 | 0 | 0 | 0 | 0 | 0 | 0
170 | 12.1935 | 11.8343 | 11.1835 | 10.8322 | 10.4612 | 10.0443 | 10.9345 | 11.949 | 12.885 | 13.0796 | 13.0478 | 13.2444 | 13.0648 | 13.1691 | 13.5095 | 13.4817 | 13.3091 | 13.4457 | 13.3028 | 13.8056 | 14.5061 | 14.4431 | 16.0585 | 16.0254
170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0839 | 1.2183 | 1.1968 | 1.127 | 1.1251 | 1.07 | 1.1007 | 1.0585 | 1.149 | 1.2565 | 0 | 0 | 0 | 0 | 0 | 0
172 | -3.2908 | -3.232 | -3.4922 | -4.2328 | -4.1084 | -3.4357 | -3.3899 | -2.6831 | -3.681 | -3.6704 | -3.8794 | -3.886 | -3.7143 | -3.4234 | -3.8505 | -3.7871 | -3.86 | -3.4094 | -3.0809 | -2.3496 | -2.4104 | -0.99809 | -0.74945 | -5.0095
172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18324 | 0.51659 | 0.5167 | 0.48064 | 0.71812 | 0.83893 | 0.827 | 0 | 0 | 0.67925 | 0.10362 | 0.4098 | 0.42977 | 0.45492 | 0.8442 | -0.9518 | 0
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18324 | 0.51659 | 0.5167 | 0.48064 | 0.71812 | 0.83893 | 0 | 0 | 0 | 0 | 0.10362 | 0.4098 | 0.42977 | 0.45492 | 0.8442 | 0 | 0
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51659 | 0.5167 | 0.48064 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4098 | 0.42977 | 0 | 0 | 0 | 0
173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.32983 | 0.92986 | 0.93007 | 0.86515 | 0 | 0 | 0 | 0 | 0 | 0 | 0.18652 | 0.73764 | 0.77359 | 0.81885 | 1.5196 | 0 | 0
174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.2858 | -0.26464 | -0.16643 | -0.027676 | 0 | 0
177 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
178 | 0 | 0 | 0 | 0 | 0 | 0 | -0.38342 | 0.20375 | 0.29639 | 0.25902 | -0.12338 | -0.12721 | -0.11801 | -0.57255 | -0.46824 | -0.56639 | 0.0067518 | 0.20449 | 0.32195 | 0.47302 | -0.0091385 | 1.0535 | -0.059706 | -0.25179
178 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20375 | 0.29639 | 0.25902 | -0.12338 | -0.12721 | -0.11801 | 0 | 0 | 0 | 0.0067518 | 0.20449 | 0.32195 | 0.47302 | -0.0091385 | 1.0535 | -0.059706 | 0
179 | 0 | 0 | 0 | 0 | 0 | 0 | 1.074 | 1.0006 | 1.0182 | 1.0166 | 1.0102 | 1.365 | 0.72743 | 1.0087 | 0 | 0 | 1.4419 | 0.61973 | 0.65107 | 0 | 0 | 0 | 0 | 0
179 | 0 | 0 | 0 | 0 | 0 | 0 | 1.074 | 1.0006 | 1.0182 | 1.0166 | 1.0102 | 0 | 0 | 0 | 0 | 0 | 0 | 0.61973 | 0.65107 | 0 | 0 | 0 | 0 | 0
181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.54842 | 0.76244 | 0.78965 | 0.62398 | 0.54061 | 0 | 0.94251 | 0.73244 | 2.0401 | 1.5508 | -0.47048 | 1.5087 | 0
181 | 0 | 0 | 0 | 0 | 0 | 0.98006 | 0.87996 | 0.64184 | 0.56728 | 0.77239 | 0.92628 | 0.54842 | 0.76244 | 0.78965 | 0.62398 | 0.54061 | 1.2282 | 0.94251 | 0.73244 | 2.0401 | 1.5508 | -0.47048 | 1.5087 | -1.4557
181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64184 | 0.56728 | 0.77239 | 0.92628 | 0.54842 | 0.76244 | 0.78965 | 0.62398 | 0.54061 | 0 | 0.94251 | 0.73244 | 2.0401 | 1.5508 | -0.47048 | 1.5087 | -1.4557
182 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20372 | 0.76621 | 0.036875 | 0.086538 | -0.047872 | 0.11167 | 0.026358 | 0.28271 | 0.68213 | 0.36966 | 0.28432 | 0.016384 | -0.18187 | 0 | 0 | 0 | 0 | 0
182 | 0 | 0 | 0 | 0 | 0 | 0 | 0.20372 | 0.76621 | 0.036875 | 0.086538 | -0.047872 | 0.11167 | 0.026358 | 0.28271 | 0.68213 | 0.36966 | 0.28432 | 0.016384 | -0.18187 | 1.0567 | -1.9672 | 1.6521 | 0 | 0
183 | 0.42459 | 1.7642 | 1.9257 | 0.031213 | 0.1178 | 0.029518 | -1.4946 | -1.2159 | -2.967 | 2.4981 | 2.2503 | 1.4825 | 1.016 | 0.99299 | 1.5541 | 1.7409 | 1.853 | -4.4958 | -2.2562 | 3.5164 | 3.17 | 3.3714 | 2.5816 | 0.82078
187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
191 | 0 | 0 | 0 | 0 | 0 | 0 | -0.75136 | -0.84723 | -1.3178 | -1.7261 | -1.3328 | -2.3098 | -2.5034 | -2.4911 | -2.4978 | -2.4914 | -2.4495 | -1.3143 | -1.4257 | -1.4715 | -0.9736 | -1.2806 | -1.375 | -1.2913
191 | 0 | 0 | 0 | 0 | 0 | 0 | -0.75136 | -0.84723 | -1.3178 | -1.7261 | -1.3328 | -2.3098 | -2.5034 | -2.4911 | -2.4978 | -2.4914 | -2.4495 | -1.3143 | -1.4257 | -1.4715 | -0.9736 | -1.2806 | -1.375 | -1.2913
191 | 0 | 0 | 0 | 0 | 0 | 0 | -0.75136 | -0.84723 | -1.3178 | -1.7261 | -1.3328 | -2.3098 | -2.5034 | -2.4911 | -2.4978 | -2.4914 | -2.4495 | -1.3143 | -1.4257 | -1.4715 | -0.9736 | -1.2806 | -1.375 | -1.2913
191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.3314 | -4.0676
192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.10273 | -1.2279 | -1.3828 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3587 | 1.9737 | 0.97182 | 0.5597 | 0.82405 | 0.79817 | 4.4115
192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3587 | 1.9737 | 0.97182 | 0.5597 | 0.82405 | 0.79817 | 0
192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3587 | 1.9737 | 0.97182 | 0.5597 | 0 | 0 | 0
194 | 0 | 0 | 0 | 0 | 0 | 0 | -5.0265 | -7.0881 | -5.0223 | -5.1855 | -3.4132 | 0.72152 | 1.1616 | 0.21901 | 1.098 | 0.7882 | 0.85689 | 1.6758 | 3.4659 | 5.5548 | 4.8935 | 6.7257 | 8.0593 | 5.9988
194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.72152 | 1.1616 | 0.21901 | 1.098 | 0.7882 | 0.85689 | 1.6758 | 3.4659 | 5.5548 | 4.8935 | 6.7257 | 8.0593 | 5.9988
194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9386 | 2.0508 | 2.6267 | 2.507 | 0 | 0 | 0
195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83122 | 1.934 | 1.3923 | 0 | 0 | 0 | 0 | 0 | 2.8436 | 1.9386 | 2.0508 | 2.6267 | 2.507 | 7.0717 | 0 | 0
195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9386 | 2.0508 | 2.6267 | 0 | 0 | 0 | 0
196 | 0.30187 | 0 | 0 | 0 | 0 | 0 | -2.2197 | -2.0918 | -2.825 | -1.5847 | -1.2559 | -1.0679 | -0.53692 | -0.015934 | 0.25099 | 0.14825 | -0.15705 | -0.85307 | -0.16287 | 0.2871 | 2.6647 | 2.715 | 8.4655 | 3.7546
196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.0679 | -0.53692 | -0.015934 | 0.25099 | 0.14825 | -0.15705 | -0.85307 | -0.16287 | 0.2871 | 2.6647 | 2.715 | 8.4655 | 3.7546
198 | 0 | 0 | 1.1036 | 0.58567 | -0.48338 | 0 | -2.4738 | -1.1465 | -0.80358 | -1.4327 | -2.996 | -2.2626 | -2.236 | -2.1482 | 0 | 0 | 0 | -0.49817 | -0.58834 | -0.43425 | -0.24495 | -0.84563 | -0.42127 | 0
198 | 0 | 0 | 1.1036 | 0.58567 | -0.48338 | 0 | -2.4738 | -1.1465 | -0.80358 | -1.4327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.49817 | -0.58834 | -0.43425 | -0.24495 | -0.84563 | -0.42127 | 0
200 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1412 | -1.7793 | -2.6077 | -2.3827 | -3.384 | -4.2634 | -3.9468 | -3.4308 | -4.1185 | -3.7311 | -4.2829 | 1.8164 | 1.7453 | 0 | 0 | 0 | 0 | 0
201 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1412 | -1.7793 | -2.6077 | -2.3827 | -3.0415 | -3.921 | -3.6044 | -3.0884 | -3.7761 | -3.7311 | -4.2829 | 1.8164 | -1.3373 | -1.0158 | -2.8177 | 7.254 | -1.1315 | -6.1056
202 | 0 | 0 | 0 | 0 | 0 | 0 | -3.1412 | -1.7793 | -2.6077 | -2.3827 | -3.2128 | -4.0922 | -3.7756 | -3.2596 | -4.1185 | -3.7311 | -4.2829 | 1.8164 | -1.3373 | -0.84454 | -2.989 | 6.7403 | -1.1315 | -6.1056
203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -15.3709 | -12.6401 | -15.1297 | -13.3192 | -35.0366 | -10.6427 | 8.7403
206 | 0 | 0 | 0 | 0 | 0 | 0 | -0.62874 | -0.40481 | 0.45892 | 0.27336 | 0.52781 | 0.89261 | 0.90683 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
207 | 0 | 0 | 0 | 0 | 0 | 0 | -0.19549 | -0.50788 | 0.21186 | 0.057127 | 0.26916 | 0.40641 | 0.75115 | 0.93414 | 0.10241 | 0 | 0 | 0.93512 | 0.79139 | 4.2363 | 4.914 | 1.5719 | 0.80655 | 0
218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.4317 | -0.54562 | -0.6838 | 0.052875 | 0.099322 | -0.14552 | 0.63183 | 1.0556 | 1.0108 | 1.243 | -0.11168 | 0.51441 | 1.2609 | 2.5998 | 3.008 | 5.4454 | 1.9521
218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.6838 | 0.052875 | 0.099322 | -0.14552 | 0.63183 | 1.0556 | 1.0108 | 1.243 | -0.11168 | 0.51441 | 1.2609 | 2.5998 | 3.008 | 5.4454 | 1.9521
218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.14552 | 0.63183 | 1.0556 | 1.0108 | 1.243 | -0.11168 | 0.51441 | 1.2609 | 2.5998 | 3.008 | 5.4454 | 1.9521
220 | 17.1293 | 4.2093 | 3.8869 | -2.8993 | -1.3201 | -0.64199 | 3.1639 | 10.3053 | 17.1277 | 21.3817 | 22.235 | 18.9319 | 17.5357 | 17.0103 | 18.2909 | 17.9467 | 22.7717 | 19.2704 | 24.34 | 26.3772 | 27.7574 | 26.3033 | 31.0597 | 35.9473
220 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1639 | 10.3053 | 17.1277 | 21.3817 | 22.235 | 18.9319 | 17.5357 | 17.0103 | 18.2909 | 17.9467 | 22.7717 | 19.2704 | 24.34 | 26.3772 | 27.7574 | 26.3033 | 31.0597 | 0
220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17.1277 | 21.3817 | 22.235 | 18.9319 | 17.5357 | 17.0103 | 18.2909 | 17.9467 | 22.7717 | 19.2704 | 24.34 | 26.3772 | 27.7574 | 26.3033 | 0 | 0
222 | 0 | 0 | 0 | 0 | 0 | 0 | -59.3953 | -36.3346 | -5.8404 | 1.3953 | 4.5349 | 7.313 | 0.33056 | -8.3167 | -2.0054 | -3.2067 | -2.2235 | 11.62 | 22.8462 | 26.2582 | 28.4375 | 0 | 0 | 0
225 | 0 | 0 | 0 | 0 | 0 | 0 | -10.7017 | -9.3022 | -13.808 | -13.6331 | -16.2683 | -17.9748 | -16.7484 | -14.7444 | -17.7452 | -16.6956 | -17.8768 | -16.903 | -21.1027 | -24.5677 | -23.9654 | -26.1884 | -23.0385 | 0
227 | 0 | 0 | 0 | 0 | 0 | 0 | -25.9545 | -22.1782 | -12.4971 | -12.7514 | -21.777 | -26.73 | -25.8777 | -25.6158 | -26.6064 | -26.215 | -26.125 | -10.7791 | -9.6987 | -8.6115 | -9.1773 | -17.6858 | -26.1145 | -26.8211
227 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12.4971 | -12.7514 | -21.777 | 0 | 0 | 0 | 0 | 0 | 0 | -10.7791 | -9.6987 | -8.6115 | -9.1773 | 0 | 0 | 0
228 | 0 | 0 | -20.5243 | 0 | 0 | 0 | 0 | 0 | -26.1248 | -26.5651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -16.7509 | -14.814 | -13.2392 | -13.3745 | -26.4198 | 0 | 0
228 | 0 | -28.0728 | -20.5243 | -27.9937 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -16.7509 | -14.814 | -13.2392 | -13.3745 | 0 | 0 | 0
229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
229 | 23.3942 | 28.8484 | 43.906 | 31.5204 | 19.3024 | 6.4539 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
230 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6403 | 10.6771 | 10.3419 | 11.6406 | 11.9239 | 10.5383 | 9.2801 | 0 | 0 | 0 | 0 | 10.8367 | 0 | 0 | 0 | 0 | 0 | 0
231 | 0 | 0 | -2.4604 | -4.3487 | 0 | 0 | 0 | -1.271 | -4.0729 | -1.998 | -0.9445 | 3.8836 | 4.2768 | 0 | 0 | 0 | 3.5135 | 0 | 0 | 0 | 0 | 9.7067 | 0 | 0
231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1.271 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
232 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -8.5356 | -0.45953 | 0 | 0 | 0 | 0 | 0
233 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -21.254 | -19.2517 | -19.3133 | -20.0544 | -21.12 | -20.7679 | 0 | 0 | 0 | -1.0444 | -9.5871 | -0.50035 | 3.7991 | 0.47527 | 2.8954 | 42.0452 | 0
234 | -43.8277 | -46.7987 | -44.0867 | -47.8052 | -41.1463 | -42.54 | -39.4543 | -28.5685 | -28.0413 | -28.075 | -30.8393 | -32.3788 | -33.2612 | -33.5204 | -33.4338 | -33.8222 | -33.6746 | -19.7616 | -17.2499 | -11.5408 | -14.0996 | -23.0945 | -32.1169 | -33.3321
235 | -44.4796 | -42.7875 | -44.7443 | -43.8124 | -41.7504 | -43.1696 | -40.028 | -28.9415 | -28.405 | -28.4392 | -31.2541 | -32.8218 | -33.7203 | -33.9843 | -33.896 | -34.2915 | -34.1412 | -19.974 | -12.6658 | -11.6038 | -14.2092 | -23.3682 | -32.5553 | -33.793
236 | -44.4796 | -42.6936 | -44.7443 | -43.8124 | -41.7504 | -43.1696 | -40.028 | -28.9415 | -28.405 | -28.4392 | -31.2541 | -32.8218 | -33.7203 | -33.9843 | -33.896 | -34.2915 | -34.1412 | -19.974 | -12.6658 | -11.6038 | -14.2092 | -23.3682 | -32.5553 | -33.793
237 | -24.5589 | -32.9809 | -34.6117 | -35.7223 | -31.7688 | -28.0846 | -26.8064 | -18.522 | -13.0165 | -12.0838 | -10.5889 | -11.5115 | -13.3782 | -14.307 | -13.976 | -13.5359 | -10.7731 | -11.2074 | -8.1737 | -7.1426 | -5.8323 | 2.2621 | -3.2365 | -13.0812
238 | -24.5552 | -32.9767 | -34.6079 | -35.7186 | -31.765 | -28.081 | -26.8027 | -18.5182 | -13.0127 | -12.08 | -10.5851 | -11.5076 | -13.3744 | -14.3032 | -13.9722 | -13.5322 | -10.7694 | -11.2036 | -8.1699 | -7.1388 | -5.8285 | 2.2659 | -3.2327 | -13.0774
239 | -81.4954 | -84.5503 | -83.3899 | -82.694 | -85.0237 | -81.5129 | -81.4105 | -80.3654 | -77.6558 | -76.1632 | -75.7996 | -75.7057 | -77.434 | -79.2323 | -77.0816 | -77.0633 | -76.3026 | -77.4048 | -71.3044 | -61.4082 | -68.0422 | -54.7331 | -74.282 | -78.6473
240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -43.9214 | -29.6581 | -26.1427 | 0 | 0 | 0 | 0
241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -17.8476 | -9.5566 | -12.3144 | -7.1587 | -9.8093 | -11.4796 | -15.122 | -12.6228 | -12.2556 | -7.8973 | -9.2613 | -9.0831 | -7.9196 | -7.0233 | 1.708 | 0 | 0
242 | -46.0463 | -54.9387 | -53.9862 | -55.4637 | -50.6936 | -47.4579 | -46.6635 | -16.5257 | -11.5334 | -9.5877 | -8.4766 | -11.4467 | -13.6449 | -18.8963 | -16.9989 | -16.0264 | -6.7368 | -6.5077 | -6.1198 | -11.3327 | -4.2338 | 3.4011 | -2.8004 | -19.4229
243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250 | -2.4649 | -2.6397 | -2.2799 | -2.5001 | -4.2968 | -2.4113 | -3.0502 | -2 | -2.6999 | -0.64148 | -1.3853 | -1.8191 | -1.4684 | -1.6626 | -1.7735 | -1.1886 | -0.78948 | -0.89322 | -1.198 | 1.6075 | 2.584 | 2.922 | 1.6461 | -5.2899
251 | -0.57867 | -0.80389 | -0.36703 | -0.62459 | -0.66207 | -0.92212 | -1.2065 | -0.71549 | -0.15642 | 0.17115 | 0.32482 | 0.3047 | 0.1862 | 0.19246 | 0.45916 | 0.50295 | 0.36706 | 0.93644 | 1.3643 | 2.3957 | 1.2547 | 1.5535 | 1.028 | 1.5854
252 | -0.67741 | -0.99619 | -0.93276 | -1.0433 | -2.1566 | -0.83116 | -0.86875 | -1.1472 | -1.646 | -1.3604 | -1.363 | -1.7853 | -1.5417 | -1.5886 | -1.7119 | -1.922 | -1.5666 | -1.4097 | -2.1303 | -1.0254 | -1.3936 | -2.673 | -1.3627 | -2.7237
253 | 3.8959 | 3.8118 | 3.9257 | 3.7826 | 3.2986 | 4.0748 | 4.009 | 3.9182 | 3.6453 | 3.9431 | 3.9827 | 3.9795 | 4.1191 | 3.9553 | 3.919 | 3.818 | 4.0362 | 3.9629 | 3.5904 | 4.3152 | 4.0357 | 3.2608 | 3.8734 | 3.0236
254 | -0.36687 | 0.2317 | -0.34349 | -0.68632 | -0.42695 | -1.8168 | -2.2238 | -2.3851 | -2.1237 | -1.7606 | -2.0725 | -2.367 | -2.391 | -2.2208 | -1.8166 | -1.7617 | -1.9133 | -3.0738 | -2.5267 | -2.108 | -1.6011 | -1.9279 | -1.4403 | -0.3509
255 | -0.92802 | -0.40195 | -0.97023 | -2.4909 | -2.4022 | -2.1348 | -1.4347 | 1.9928 | 1.759 | 4.6677 | 3.6491 | 3.5329 | 2.9286 | 2.3766 | 2.8708 | 2.9115 | 3.1319 | 3.0994 | 5.4284 | 8.3243 | 7.8746 | 7.4565 | 4.7937 | -0.038284
262 | 2.6596 | 2.3175 | 2.1845 | 2.6878 | 1.5697 | 2.1042 | 2.0958 | 1.9296 | 3.1301 | 2.6569 | 2.0602 | 3.1323 | 2.5333 | 2.2719 | 3.2905 | 2.4839 | 2.2841 | 3.0282 | 3.0055 | 2.8321 | 3.4672 | 3.2108 | 4.8706 | 3.4591
263 | -2.8354 | -2.503 | -2.573 | -2.2706 | -1.8634 | -1.5525 | -1.0579 | -2.05 | -1.3765 | -1.5729 | -0.88667 | -1.2331 | -1.503 | -2.102 | -2.0398 | -1.9906 | -1.1443 | -2.1844 | -1.2511 | -1.3557 | -1.5061 | -1.6736 | -1.7445 | -2.022
264 | -8.7095 | -10.0851 | -10.1489 | -10.344 | -8.2171 | -10.0274 | -9.1166 | -9.0596 | -9.1421 | -9.3485 | -9.7389 | -8.6382 | -8.7121 | -9.9379 | -9.9278 | -9.9437 | -10.3348 | -9.4121 | -6.7585 | -6.6526 | -6.3691 | -6.4232 | -5.6285 | -6.8311
265 | 7.7384 | 7.2501 | 6.5581 | 5.562 | 6.1887 | 6.2501 | 6.6101 | 7.3953 | 6.7451 | 6.9303 | 7.866 | 6.9979 | 7.805 | 7.6455 | 7.0796 | 7.9452 | 7.9475 | 7.1352 | 6.9544 | 8.5173 | 7.1227 | 11.086 | 12.3097 | 8.8687
266 | -2.2248 | -2.23 | -2.0549 | -2.1581 | -1.8894 | -1.8497 | -2.6006 | -1.676 | -2.5618 | -2.0365 | -2.3669 | -2.2596 | -1.5772 | -0.94216 | -1.1743 | -1.5013 | -2.2263 | -0.61943 | -2.3068 | -1.8045 | -2.2376 | -2.8753 | 1.0428 | -1.7828
267 | -6.6222 | -6.6004 | -6.965 | -7.9474 | -10.552 | -7.8406 | -8.6874 | -8.6002 | -7.4239 | -6.9473 | -7.366 | -6.5311 | -6.492 | -5.8387 | -5.8339 | -6.4786 | -6.9562 | -6.8671 | -4.185 | -5.1779 | -4.5401 | -2.4725 | -5.2208 | 1.5468
268 | 3.0907 | -0.50218 | 0.6305 | -0.99494 | 0.7284 | -1.9662 | 0.26732 | 4.2825 | 3.5584 | 6.1291 | 8.7398 | 14.3944 | 14.1989 | 12.677 | 16.8452 | 14.964 | 13.9389 | 9.3956 | 18.2057 | 30.8649 | 27.7572 | 23.405 | 30.7569 | 26.2698
273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6679 | 0.70756 | 0.61342 | 0.63066 | 0.65239 | 0.80804 | 0.87122 | 1.0837 | 1.0488 | 0.63411 | 0.51244 | 0.47563
273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0837 | 1.0488 | 0.63411 | 0.51244 | 0.47563
273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.27122 | 0.55248 | 0.58844 | 0.38322 | 0.41352 | 0.6679 | 0.70756 | 0.61342 | 0.63066 | 0.65239 | 0.80804 | 0.87122 | 1.0837 | 1.0488 | 0.63411 | 0.51244 | 0.47563
293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Gen_Vg
bus | t1 | t2 | t3 | t4 | t5 | t6 | t7 | t8 | t9 | t10 | t11 | t12 | t13 | t14 | t15 | t16 | t17 | t18 | t19 | t20 | t21 | t22 | t23 | t24
1 | 1.0407 | 1.0454 | 1.048 | 1.0458 | 1.0362 | 1.0232 | 1.0284 | 1.0415 | 1.0426 | 1.0423 | 1.0426 | 1.0403 | 1.0392 | 1.0413 | 1.0454 | 1.0457 | 1.0468 | 1.0451 | 1.0439 | 1.0431 | 1.0444 | 1.0467 | 1.0489 | 1.0487
2 | 1.0314 | 1.0335 | 1.0338 | 1.0317 | 1.0267 | 1.0215 | 1.0301 | 1.0388 | 1.0412 | 1.0421 | 1.044 | 1.0453 | 1.0453 | 1.0445 | 1.0458 | 1.0455 | 1.0458 | 1.0459 | 1.047 | 1.048 | 1.0478 | 1.0481 | 1.0482 | 1.0473
3 | 1.0386 | 1.0344 | 1.0336 | 1.032 | 1.0301 | 1.0308 | 1.0326 | 1.0408 | 1.0418 | 1.0415 | 1.042 | 1.0418 | 1.0415 | 1.0405 | 1.0415 | 1.0412 | 1.0418 | 1.0422 | 1.0424 | 1.0428 | 1.0433 | 1.0444 | 1.0442 | 1.0406
4 | 1.0332 | 1.031 | 1.0298 | 1.0307 | 1.0315 | 1.0302 | 1.0293 | 1.0339 | 1.0352 | 1.0376 | 1.0361 | 1.0358 | 1.0356 | 1.0358 | 1.0362 | 1.0362 | 1.0362 | 1.0389 | 1.0411 | 1.0431 | 1.0429 | 1.0392 | 1.0359 | 1.0352
5 | 1.0405 | 1.0409 | 1.0406 | 1.0337 | 1.0248 | 1.0165 | 1.018 | 1.0274 | 1.0299 | 1.0291 | 1.0269 | 1.0288 | 1.0269 | 1.0356 | 1.0389 | 1.0396 | 1.0366 | 1.033 | 1.034 | 1.0411 | 1.0418 | 1.0449 | 1.0477 | 1.0467
6 | 1.0402 | 1.0405 | 1.0402 | 1.0334 | 1.0246 | 1.0164 | 1.018 | 1.0274 | 1.0299 | 1.0291 | 1.0269 | 1.0287 | 1.0269 | 1.0354 | 1.0386 | 1.0394 | 1.0364 | 1.0329 | 1.0339 | 1.0408 | 1.0415 | 1.0445 | 1.0475 | 1.0462
7 | 1.0328 | 1.0309 | 1.0311 | 1.031 | 1.0307 | 1.0304 | 1.0283 | 1.0392 | 1.0361 | 1.0345 | 1.0342 | 1.0341 | 1.0338 | 1.035 | 1.0338 | 1.0338 | 1.034 | 1.0384 | 1.0369 | 1.0372 | 1.037 | 1.0358 | 1.034 | 1.0327
22 | 1.026 | 1.0249 | 1.0246 | 1.0249 | 1.023 | 1.0245 | 1.0266 | 1.027 | 1.031 | 1.0317 | 1.0305 | 1.0313 | 1.0311 | 1.0303 | 1.0308 | 1.0306 | 1.0304 | 1.0318 | 1.0309 | 1.0307 | 1.0306 | 1.0301 | 1.029 | 1.0272
30 | 1.0172 | 1.0173 | 1.0172 | 1.0155 | 1.0133 | 1.013 | 1.0348 | 1.0389 | 1.04 | 1.0399 | 1.0395 | 1.0345 | 1.0336 | 1.0331 | 1.0303 | 1.0304 | 1.0341 | 1.0389 | 1.0409 | 1.0349 | 1.0335 | 1.0309 | 1.025 | 1.021
61 | 1.0186 | 1.0187 | 1.0196 | 1.0168 | 1.0125 | 1.0103 | 1.0186 | 1.0266 | 1.0295 | 1.03 | 1.0303 | 1.0303 | 1.0302 | 1.0291 | 1.0308 | 1.0308 | 1.0319 | 1.0311 | 1.0299 | 1.0297 | 1.0311 | 1.0331 | 1.0312 | 1.0269
108 | 1.0077 | 1.0124 | 1.008 | 1.0104 | 1.0072 | 1.0074 | 1.017 | 1.0161 | 1.017 | 1.017 | 1.0168 | 1.0174 | 1.0167 | 1.0164 | 1.0146 | 1.0147 | 1.0174 | 1.0164 | 1.0179 | 1.0161 | 1.0156 | 1.0146 | 1.0127 | 1.011
109 | 1.0139 | 1.0129 | 1.0106 | 1.0103 | 1.0071 | 1.0067 | 1.0105 | 1.0157 | 1.0191 | 1.0224 | 1.0222 | 1.0219 | 1.0217 | 1.0215 | 1.0228 | 1.0213 | 1.0232 | 1.0242 | 1.0228 | 1.0214 | 1.0211 | 1.0206 | 1.0194 | 1.0168
110 | 1.0179 | 1.0173 | 1.0159 | 1.0158 | 1.015 | 1.0151 | 1.0147 | 1.0188 | 1.0198 | 1.0224 | 1.0225 | 1.023 | 1.0228 | 1.0244 | 1.0236 | 1.0233 | 1.023 | 1.0231 | 1.0222 | 1.0231 | 1.0228 | 1.0219 | 1.0205 | 1.0193
111 | 1.0148 | 1.016 | 1.0173 | 1.0148 | 1.0102 | 1.0086 | 1.0152 | 1.0223 | 1.0242 | 1.0245 | 1.025 | 1.0249 | 1.0251 | 1.0243 | 1.026 | 1.0261 | 1.027 | 1.0255 | 1.0229 | 1.0239 | 1.0247 | 1.0253 | 1.0233 | 1.0202
112 | 1.0119 | 1.0099 | 1.0111 | 1.0085 | 1.0069 | 1.009 | 1.0156 | 1.018 | 1.0211 | 1.0205 | 1.0195 | 1.0189 | 1.0183 | 1.0194 | 1.0192 | 1.0183 | 1.0191 | 1.0245 | 1.0269 | 1.025 | 1.0246 | 1.0236 | 1.0202 | 1.015
113 | 1.0217 | 1.0211 | 1.0205 | 1.0214 | 1.02 | 1.0203 | 1.0234 | 1.0271 | 1.0291 | 1.0282 | 1.0259 | 1.025 | 1.0249 | 1.0246 | 1.025 | 1.025 | 1.0251 | 1.0301 | 1.0315 | 1.0298 | 1.0297 | 1.0284 | 1.0267 | 1.0248
114 | 1.0163 | 1.0148 | 1.014 | 1.0125 | 1.0092 | 1.009 | 1.0116 | 1.0168 | 1.0231 | 1.024 | 1.0237 | 1.0234 | 1.0226 | 1.0229 | 1.0238 | 1.0239 | 1.0252 | 1.0276 | 1.0276 | 1.0274 | 1.0269 | 1.0273 | 1.0253 | 1.021
115 | 1.0186 | 1.0166 | 1.0128 | 1.0112 | 1.0068 | 1.0056 | 1.0056 | 1.0104 | 1.0083 | 1.0072 | 1.0045 | 1.0052 | 1.0037 | 1.0103 | 1.0101 | 1.0111 | 1.0084 | 1.007 | 1.0075 | 1.0114 | 1.0113 | 1.0117 | 1.0155 | 1.0139
116 | 1.0138 | 1.0131 | 1.013 | 1.0123 | 1.0097 | 1.0083 | 1.0119 | 1.0145 | 1.0173 | 1.0172 | 1.0177 | 1.0186 | 1.0185 | 1.018 | 1.0179 | 1.018 | 1.0192 | 1.0187 | 1.0205 | 1.0206 | 1.0216 | 1.0198 | 1.0182 | 1.0164
117 | 1.0144 | 1.014 | 1.0129 | 1.0137 | 1.0102 | 1.0129 | 1.0155 | 1.0208 | 1.0183 | 1.015 | 1.0144 | 1.0158 | 1.0159 | 1.0156 | 1.0159 | 1.016 | 1.0141 | 1.0189 | 1.0174 | 1.0157 | 1.0158 | 1.0159 | 1.0154 | 1.0138
118 | 1.0238 | 1.0225 | 1.0214 | 1.0179 | 1.0133 | 1.0106 | 1.0124 | 1.0181 | 1.0198 | 1.0195 | 1.0182 | 1.0183 | 1.0171 | 1.0198 | 1.0207 | 1.0211 | 1.0207 | 1.0219 | 1.0223 | 1.0234 | 1.0232 | 1.0245 | 1.0245 | 1.0219
119 | 1.029 | 1.0282 | 1.0284 | 1.0283 | 1.0264 | 1.0259 | 1.0297 | 1.0309 | 1.0324 | 1.0341 | 1.0339 | 1.0337 | 1.0339 | 1.0339 | 1.0342 | 1.0343 | 1.0342 | 1.0349 | 1.037 | 1.0348 | 1.035 | 1.0349 | 1.0334 | 1.031
120 | 1.0142 | 1.0136 | 1.0142 | 1.0125 | 1.0091 | 1.0084 | 1.0126 | 1.0198 | 1.0224 | 1.023 | 1.0237 | 1.0239 | 1.0241 | 1.0229 | 1.0245 | 1.0244 | 1.0252 | 1.0252 | 1.0237 | 1.0239 | 1.0247 | 1.0257 | 1.0239 | 1.0208
121 | 1.0164 | 1.0167 | 1.0163 | 1.0164 | 1.0149 | 1.0154 | 1.0162 | 1.0168 | 1.0196 | 1.0204 | 1.0199 | 1.021 | 1.0211 | 1.0205 | 1.021 | 1.021 | 1.0209 | 1.0192 | 1.0195 | 1.0199 | 1.0199 | 1.0196 | 1.0187 | 1.0173
122 | 1.0258 | 1.0233 | 1.0234 | 1.0221 | 1.0188 | 1.0192 | 1.0217 | 1.0302 | 1.032 | 1.0349 | 1.0356 | 1.034 | 1.0334 | 1.031 | 1.0328 | 1.033 | 1.0352 | 1.0336 | 1.0364 | 1.034 | 1.0344 | 1.035 | 1.0331 | 1.0287
123 | 1.0189 | 1.0183 | 1.0185 | 1.0161 | 1.0142 | 1.0172 | 1.0213 | 1.0249 | 1.0273 | 1.0244 | 1.0236 | 1.0251 | 1.024 | 1.0235 | 1.024 | 1.0232 | 1.0235 | 1.0283 | 1.0302 | 1.0269 | 1.0269 | 1.0263 | 1.0243 | 1.0207
124 | 1.0149 | 1.0109 | 1.0097 | 1.0085 | 1.0068 | 1.0085 | 1.0118 | 1.0207 | 1.0251 | 1.0286 | 1.0293 | 1.0296 | 1.0285 | 1.0277 | 1.0285 | 1.0284 | 1.029 | 1.0311 | 1.0312 | 1.0298 | 1.0297 | 1.0307 | 1.0281 | 1.0223
125 | 1.0164 | 1.0155 | 1.0144 | 1.0139 | 1.0125 | 1.0125 | 1.0145 | 1.016 | 1.0203 | 1.0229 | 1.0234 | 1.0239 | 1.0223 | 1.0222 | 1.0214 | 1.0211 | 1.0235 | 1.0237 | 1.0239 | 1.0229 | 1.0228 | 1.0205 | 1.0192 | 1.0177
126 | 1.0255 | 1.0244 | 1.0242 | 1.0239 | 1.0214 | 1.0235 | 1.0269 | 1.0307 | 1.0303 | 1.0303 | 1.0287 | 1.028 | 1.028 | 1.0275 | 1.028 | 1.028 | 1.0282 | 1.0317 | 1.033 | 1.0309 | 1.0308 | 1.0301 | 1.0287 | 1.0266
127 | 1.0157 | 1.0155 | 1.0163 | 1.0133 | 1.0088 | 1.0076 | 1.012 | 1.0191 | 1.022 | 1.0224 | 1.0225 | 1.0233 | 1.0232 | 1.0218 | 1.0235 | 1.0236 | 1.0241 | 1.0234 | 1.0236 | 1.0219 | 1.0226 | 1.0236 | 1.0224 | 1.0191
128 | 1.0274 | 1.0266 | 1.0244 | 1.026 | 1.0201 | 1.0168 | 1.0251 | 1.0304 | 1.033 | 1.0348 | 1.0374 | 1.0355 | 1.0352 | 1.0349 | 1.0336 | 1.0337 | 1.0355 | 1.0366 | 1.0381 | 1.037 | 1.037 | 1.0361 | 1.0338 | 1.0303
129 | 1.0239 | 1.0211 | 1.02 | 1.0175 | 1.0151 | 1.0147 | 1.0207 | 1.026 | 1.0298 | 1.0306 | 1.0343 | 1.0347 | 1.0348 | 1.0338 | 1.0349 | 1.035 | 1.0357 | 1.0325 | 1.0322 | 1.0328 | 1.0338 | 1.0352 | 1.0342 | 1.0298
130 | 1.0119 | 1.0112 | 1.0124 | 1.0102 | 1.0081 | 1.0083 | 1.011 | 1.0142 | 1.0168 | 1.0188 | 1.0194 | 1.0196 | 1.0186 | 1.0189 | 1.0197 | 1.0198 | 1.0206 | 1.019 | 1.0202 | 1.0209 | 1.0226 | 1.0205 | 1.0181 | 1.0156
131 | 1.0243 | 1.0231 | 1.0237 | 1.0236 | 1.0217 | 1.021 | 1.0224 | 1.0275 | 1.0264 | 1.0257 | 1.0271 | 1.0267 | 1.0264 | 1.0256 | 1.0263 | 1.0264 | 1.0268 | 1.0278 | 1.0299 | 1.0276 | 1.0274 | 1.0277 | 1.026 | 1.0241
132 | 1.0095 | 1.0097 | 1.0093 | 1.0097 | 1.0074 | 1.006 | 1.0085 | 1.0124 | 1.0121 | 1.014 | 1.014 | 1.0133 | 1.0127 | 1.0123 | 1.013 | 1.0131 | 1.0142 | 1.0122 | 1.012 | 1.0122 | 1.0126 | 1.0131 | 1.0125 | 1.0105
133 | 1.0014 | 1.0022 | 1.0021 | 1.0032 | 1.0015 | 1.0013 | 1.0089 | 1.0077 | 1.0077 | 1.0073 | 1.0069 | 1.0074 | 1.0068 | 1.0065 | 1.0049 | 1.005 | 1.0073 | 1.0062 | 1.0072 | 1.0067 | 1.0064 | 1.0057 | 1.0044 | 1.0034
134 | 1.0108 | 1.0108 | 1.0121 | 1.0091 | 1.0062 | 1.0052 | 1.0095 | 1.0181 | 1.0218 | 1.0225 | 1.0232 | 1.0234 | 1.0232 | 1.0222 | 1.0226 | 1.0226 | 1.0234 | 1.0228 | 1.0237 | 1.022 | 1.0228 | 1.0232 | 1.0213 | 1.0177
136 | 1.0231 | 1.0228 | 1.0214 | 1.0217 | 1.0184 | 1.0209 | 1.0188 | 1.0217 | 1.0233 | 1.0256 | 1.0256 | 1.0261 | 1.0261 | 1.0277 | 1.0269 | 1.0265 | 1.0262 | 1.0263 | 1.029 | 1.0281 | 1.0277 | 1.0272 | 1.0255 | 1.0236
137 | 1.0216 | 1.0228 | 1.0198 | 1.0223 | 1.0171 | 1.0161 | 1.0178 | 1.0249 | 1.0254 | 1.0285 | 1.0288 | 1.027 | 1.0269 | 1.0258 | 1.0278 | 1.0279 | 1.0297 | 1.0283 | 1.0283 | 1.027 | 1.0275 | 1.028 | 1.0271 | 1.025
138 | 1.0138 | 1.0146 | 1.0157 | 1.0132 | 1.0102 | 1.0085 | 1.0141 | 1.0223 | 1.0227 | 1.0234 | 1.0232 | 1.0242 | 1.0234 | 1.0232 | 1.0244 | 1.0244 | 1.025 | 1.0238 | 1.0256 | 1.0238 | 1.0247 | 1.0254 | 1.0233 | 1.0201
139 | 1.0185 | 1.018 | 1.0164 | 1.0169 | 1.0155 | 1.016 | 1.0141 | 1.0188 | 1.0196 | 1.0224 | 1.0223 | 1.0229 | 1.0227 | 1.0242 | 1.0236 | 1.0231 | 1.0228 | 1.0231 | 1.0217 | 1.0225 | 1.0221 | 1.0219 | 1.0207 | 1.0197
140 | 1.0129 | 1.0123 | 1.0131 | 1.0136 | 1.0127 | 1.0139 | 1.0168 | 1.0174 | 1.0248 | 1.0255 | 1.021 | 1.0192 | 1.019 | 1.0189 | 1.0229 | 1.0226 | 1.0221 | 1.0273 | 1.0227 | 1.0201 | 1.02 | 1.0191 | 1.0177 | 1.0161
141 | 1.0153 | 1.0109 | 1.0136 | 1.0101 | 1.0102 | 1.01 | 1.0159 | 1.0208 | 1.0216 | 1.0179 | 1.0172 | 1.0164 | 1.0169 | 1.0166 | 1.017 | 1.0172 | 1.0175 | 1.0216 | 1.0206 | 1.019 | 1.019 | 1.0187 | 1.0173 | 1.0149
142 | 1.0122 | 1.0124 | 1.0126 | 1.0108 | 1.009 | 1.0077 | 1.02 | 1.0223 | 1.0225 | 1.0264 | 1.0261 | 1.0229 | 1.0244 | 1.0241 | 1.0246 | 1.0246 | 1.0227 | 1.0254 | 1.0267 | 1.0256 | 1.0251 | 1.0234 | 1.0204 | 1.0168
144 | 1.0121 | 1.012 | 1.0107 | 1.0098 | 1.007 | 1.0059 | 1.0118 | 1.0188 | 1.0218 | 1.0225 | 1.0231 | 1.0233 | 1.0232 | 1.0215 | 1.0232 | 1.0228 | 1.0237 | 1.0235 | 1.0224 | 1.0212 | 1.0217 | 1.0224 | 1.0209 | 1.018
145 | 1.0107 | 1.0096 | 1.0096 | 1.011 | 1.0083 | 1.0072 | 1.0106 | 1.0175 | 1.0183 | 1.0208 | 1.0214 | 1.0206 | 1.0201 | 1.0182 | 1.0194 | 1.0197 | 1.021 | 1.0193 | 1.0183 | 1.0178 | 1.0193 | 1.0217 | 1.0199 | 1.016
146 | 1.0121 | 1.0153 | 1.015 | 1.0153 | 1.0121 | 1.0149 | 1.0169 | 1.013 | 1.0171 | 1.0177 | 1.0165 | 1.0172 | 1.017 | 1.0163 | 1.0167 | 1.0165 | 1.0163 | 1.018 | 1.0163 | 1.0156 | 1.0156 | 1.0154 | 1.0149 | 1.014
147 | 1.0216 | 1.0211 | 1.0216 | 1.0218 | 1.0202 | 1.0195 | 1.0233 | 1.0241 | 1.0252 | 1.0239 | 1.0234 | 1.0273 | 1.0233 | 1.0231 | 1.0234 | 1.0236 | 1.0236 | 1.0246 | 1.027 | 1.0254 | 1.0255 | 1.025 | 1.0238 | 1.0225
149 | 1.0162 | 1.0162 | 1.0166 | 1.0168 | 1.0134 | 1.0158 | 1.0144 | 1.0147 | 1.0168 | 1.0178 | 1.0176 | 1.0201 | 1.0204 | 1.019 | 1.0203 | 1.0204 | 1.0203 | 1.0187 | 1.0219 | 1.021 | 1.021 | 1.0202 | 1.0187 | 1.0167
150 | 1.0164 | 1.0167 | 1.0158 | 1.014 | 1.0117 | 1.0112 | 1.0156 | 1.0191 | 1.022 | 1.0222 | 1.0226 | 1.0249 | 1.0257 | 1.0248 | 1.0252 | 1.0239 | 1.0226 | 1.023 | 1.0266 | 1.0236 | 1.0264 | 1.0248 | 1.0228 | 1.0176
151 | 1.0155 | 1.0151 | 1.014 | 1.0126 | 1.011 | 1.0126 | 1.0249 | 1.0263 | 1.0267 | 1.0285 | 1.0283 | 1.025 | 1.0248 | 1.0247 | 1.0226 | 1.0228 | 1.0252 | 1.0281 | 1.0281 | 1.0272 | 1.0266 | 1.0248 | 1.0212 | 1.0175
152 | 1.0224 | 1.0207 | 1.0198 | 1.0167 | 1.0137 | 1.0142 | 1.0146 | 1.0161 | 1.0175 | 1.0195 | 1.0185 | 1.0201 | 1.0187 | 1.0212 | 1.0219 | 1.0214 | 1.0206 | 1.02 | 1.0215 | 1.0205 | 1.0205 | 1.0215 | 1.022 | 1.0201
153 | 1.0179 | 1.0164 | 1.0166 | 1.0139 | 1.0115 | 1.0079 | 1.0155 | 1.0221 | 1.0237 | 1.0204 | 1.0217 | 1.0249 | 1.025 | 1.0246 | 1.0257 | 1.0256 | 1.0259 | 1.028 | 1.0275 | 1.026 | 1.0259 | 1.0265 | 1.0265 | 1.0261
154 | 1.0123 | 1.0118 | 1.011 | 1.0103 | 1.0095 | 1.012 | 1.0113 | 1.014 | 1.0145 | 1.016 | 1.0162 | 1.0164 | 1.0161 | 1.0177 | 1.017 | 1.0169 | 1.0168 | 1.0172 | 1.0176 | 1.0176 | 1.0174 | 1.0159 | 1.0148 | 1.0135
155 | 1.0232 | 1.0217 | 1.0197 | 1.0163 | 1.012 | 1.0101 | 1.0123 | 1.0154 | 1.0179 | 1.0172 | 1.0153 | 1.0165 | 1.0161 | 1.0199 | 1.0216 | 1.0222 | 1.0203 | 1.0203 | 1.0212 | 1.0233 | 1.0236 | 1.0261 | 1.0283 | 1.0238
156 | 1.0146 | 1.014 | 1.0139 | 1.011 | 1.0074 | 1.0064 | 1.0127 | 1.0175 | 1.0192 | 1.0183 | 1.0192 | 1.0202 | 1.0202 | 1.0192 | 1.0212 | 1.021 | 1.022 | 1.0207 | 1.0204 | 1.0195 | 1.0201 | 1.0214 | 1.0208 | 1.0178
157 | 1.0111 | 1.0122 | 1.0133 | 1.0108 | 1.0077 | 1.009 | 1.0111 | 1.0184 | 1.0162 | 1.0212 | 1.0217 | 1.0215 | 1.0173 | 1.0209 | 1.0183 | 1.0184 | 1.0193 | 1.0177 | 1.0197 | 1.0183 | 1.0192 | 1.0199 | 1.0184 | 1.016
158 | 1.021 | 1.0205 | 1.0209 | 1.0192 | 1.0175 | 1.0165 | 1.0213 | 1.0246 | 1.0293 | 1.0283 | 1.0284 | 1.0274 | 1.0272 | 1.0255 | 1.0272 | 1.0273 | 1.0288 | 1.0302 | 1.0288 | 1.027 | 1.0274 | 1.0281 | 1.0273 | 1.0252
159 | 1.0259 | 1.0241 | 1.0247 | 1.0242 | 1.0206 | 1.0231 | 1.0274 | 1.0241 | 1.0272 | 1.0296 | 1.0284 | 1.0287 | 1.0285 | 1.0277 | 1.0284 | 1.0284 | 1.0286 | 1.0285 | 1.0298 | 1.0289 | 1.0288 | 1.0282 | 1.0271 | 1.0253
160 | 1.0183 | 1.0181 | 1.0183 | 1.0184 | 1.0144 | 1.0127 | 1.0189 | 1.0228 | 1.0248 | 1.0246 | 1.0258 | 1.0263 | 1.026 | 1.0282 | 1.027 | 1.0266 | 1.0293 | 1.028 | 1.0289 | 1.0282 | 1.0284 | 1.0301 | 1.0299 | 1.0263
161 | 1.0155 | 1.0136 | 1.0147 | 1.0116 | 1.0077 | 1.0064 | 1.0099 | 1.0133 | 1.018 | 1.0191 | 1.0184 | 1.0177 | 1.0164 | 1.0164 | 1.0177 | 1.0177 | 1.0193 | 1.0186 | 1.0177 | 1.0185 | 1.0179 | 1.0198 | 1.0185 | 1.0145
162 | 1.0181 | 1.0185 | 1.0179 | 1.0183 | 1.0135 | 1.0126 | 1.0147 | 1.0182 | 1.0204 | 1.0199 | 1.0197 | 1.0212 | 1.0218 | 1.0213 | 1.0218 | 1.0207 | 1.018 | 1.0204 | 1.0228 | 1.021 | 1.0209 | 1.0201 | 1.0196 | 1.0157
163 | 1.0168 | 1.0176 | 1.0169 | 1.015 | 1.011 | 1.0111 | 1.0265 | 1.0273 | 1.0286 | 1.0286 | 1.0278 | 1.0241 | 1.0252 | 1.0249 | 1.0225 | 1.0225 | 1.0239 | 1.0262 | 1.0289 | 1.0227 | 1.0217 | 1.02 | 1.0166 | 1.0145
164 | 1.0267 | 1.0253 | 1.0218 | 1.021 | 1.0248 | 1.0243 | 1.0215 | 1.0264 | 1.0245 | 1.0263 | 1.0244 | 1.024 | 1.0239 | 1.0239 | 1.0241 | 1.0241 | 1.0241 | 1.0282 | 1.0254 | 1.0276 | 1.0275 | 1.0261 | 1.0253 | 1.025
165 | 1.007 | 1.0068 | 1.0073 | 1.006 | 1.0037 | 1.0029 | 1.0052 | 1.0061 | 1.0071 | 1.0075 | 1.0085 | 1.0106 | 1.0105 | 1.0096 | 1.0105 | 1.0104 | 1.0109 | 1.0103 | 1.0107 | 1.0098 | 1.0101 | 1.0106 | 1.0098 | 1.0092
166 | 1.0053 | 1.0062 | 1.0042 | 1.0036 | 1.0009 | 1.003 | 1.005 | 1.0072 | 1.0123 | 1.0152 | 1.0201 | 1.0204 | 1.0193 | 1.0192 | 1.0193 | 1.0192 | 1.0197 | 1.0219 | 1.0232 | 1.021 | 1.0205 | 1.021 | 1.0174 | 1.0122
167 | 1.0082 | 1.0078 | 1.0084 | 1.0088 | 1.0055 | 1.0038 | 1.0071 | 1.0107 | 1.0102 | 1.0104 | 1.01 | 1.0109 | 1.0105 | 1.01 | 1.0107 | 1.0105 | 1.0113 | 1.0108 | 1.0109 | 1.0097 | 1.01 | 1.0106 | 1.01 | 1.009
168 | 1.0247 | 1.0206 | 1.019 | 1.0195 | 1.0191 | 1.0186 | 1.0211 | 1.0217 | 1.0273 | 1.0303 | 1.0302 | 1.0309 | 1.0261 | 1.0276 | 1.0271 | 1.0265 | 1.0272 | 1.0309 | 1.0298 | 1.03 | 1.0297 | 1.029 | 1.0272 | 1.0251
169 | 1.0253 | 1.0242 | 1.0238 | 1.0233 | 1.0203 | 1.0223 | 1.0245 | 1.0256 | 1.0235 | 1.0248 | 1.024 | 1.0258 | 1.0254 | 1.0241 | 1.0253 | 1.0253 | 1.0255 | 1.0239 | 1.0278 | 1.0272 | 1.0271 | 1.0266 | 1.0255 | 1.0237
170 | 1.0178 | 1.0164 | 1.0196 | 1.0167 | 1.0123 | 1.0102 | 1.0125 | 1.018 | 1.0182 | 1.0205 | 1.0196 | 1.019 | 1.0179 | 1.0194 | 1.0201 | 1.0203 | 1.0209 | 1.0188 | 1.0192 | 1.0201 | 1.0196 | 1.0204 | 1.02 | 1.018
171 | 1.0124 | 1.0141 | 1.0143 | 1.013 | 1.0092 | 1.0078 | 1.0081 | 1.0129 | 1.0152 | 1.0139 | 1.0144 | 1.0171 | 1.0183 | 1.0181 | 1.0181 | 1.017 | 1.0131 | 1.0141 | 1.02 | 1.0161 | 1.016 | 1.0151 | 1.0147 | 1.011
172 | 1.0064 | 1.006 | 1.0065 | 1.0074 | 1.0043 | 1.0033 | 1.0057 | 1.0071 | 1.0081 | 1.0083 | 1.0087 | 1.01 | 1.0098 | 1.0089 | 1.0099 | 1.0098 | 1.0105 | 1.01 | 1.01 | 1.009 | 1.0093 | 1.0098 | 1.0093 | 1.0085
173 | 1.0178 | 1.018 | 1.0177 | 1.016 | 1.0137 | 1.0133 | 1.0359 | 1.0415 | 1.0431 | 1.043 | 1.0423 | 1.0363 | 1.0354 | 1.0348 | 1.0319 | 1.0319 | 1.0357 | 1.041 | 1.0438 | 1.0379 | 1.0359 | 1.0328 | 1.0255 | 1.021
174 | 1.0176 | 1.0178 | 1.0176 | 1.0159 | 1.0136 | 1.0132 | 1.0355 | 1.0406 | 1.0419 | 1.0418 | 1.0413 | 1.0357 | 1.0348 | 1.0342 | 1.0314 | 1.0314 | 1.0352 | 1.0403 | 1.0427 | 1.0368 | 1.035 | 1.0321 | 1.0254 | 1.021
175 | 1.0065 | 1.0056 | 1.0049 | 1.0075 | 1.0038 | 1.004 | 1.0048 | 1.0083 | 1.0088 | 1.0097 | 1.0096 | 1.0093 | 1.009 | 1.0102 | 1.0101 | 1.01 | 1.0104 | 1.0114 | 1.0092 | 1.0081 | 1.008 | 1.0076 | 1.0072 | 1.0066
176 | 1.0064 | 1.0056 | 1.0049 | 1.0075 | 1.0037 | 1.004 | 1.0048 | 1.0083 | 1.0088 | 1.0096 | 1.0095 | 1.0093 | 1.0089 | 1.0102 | 1.01 | 1.01 | 1.0103 | 1.0113 | 1.0091 | 1.0081 | 1.0079 | 1.0076 | 1.0072 | 1.0065
177 | 1.0179 | 1.0182 | 1.0179 | 1.0162 | 1.0139 | 1.0134 | 1.0361 | 1.0411 | 1.0425 | 1.0424 | 1.0418 | 1.0363 | 1.0354 | 1.0349 | 1.0322 | 1.0322 | 1.0359 | 1.0407 | 1.0446 | 1.0396 | 1.0374 | 1.0338 | 1.0253 | 1.0211
178 | 1.007 | 1.0072 | 1.0081 | 1.0053 | 1.0038 | 1.0031 | 1.0128 | 1.0274 | 1.0262 | 1.0266 | 1.0257 | 1.0164 | 1.0163 | 1.0135 | 1.011 | 1.0158 | 1.0277 | 1.0275 | 1.0266 | 1.0267 | 1.0269 | 1.0271 | 1.0268 | 1.0121
179 | 1.0172 | 1.0173 | 1.0172 | 1.0156 | 1.0133 | 1.013 | 1.0395 | 1.0436 | 1.0447 | 1.0446 | 1.0442 | 1.0369 | 1.0355 | 1.035 | 1.0303 | 1.0304 | 1.0367 | 1.0435 | 1.0455 | 1.0349 | 1.0335 | 1.0309 | 1.0251 | 1.021
181 | 1.0232 | 1.0232 | 1.0225 | 1.0207 | 1.017 | 1.0171 | 1.0189 | 1.0243 | 1.0282 | 1.0281 | 1.0285 | 1.032 | 1.0325 | 1.032 | 1.0324 | 1.0308 | 1.0256 | 1.0298 | 1.0378 | 1.0359 | 1.0355 | 1.0336 | 1.0331 | 1.0242
182 | 1.0178 | 1.018 | 1.0177 | 1.0161 | 1.0137 | 1.0133 | 1.0364 | 1.0414 | 1.0427 | 1.0426 | 1.042 | 1.0366 | 1.0357 | 1.0352 | 1.0325 | 1.0325 | 1.0361 | 1.0409 | 1.0434 | 1.0373 | 1.0355 | 1.0323 | 1.0252 | 1.0209
183 | 1.0358 | 1.0347 | 1.0344 | 1.0339 | 1.0322 | 1.0335 | 1.0395 | 1.0451 | 1.0448 | 1.0441 | 1.0425 | 1.0418 | 1.0416 | 1.0411 | 1.0417 | 1.0418 | 1.042 | 1.0461 | 1.0463 | 1.0451 | 1.045 | 1.0441 | 1.0423 | 1.0395
187 | 1.0142 | 1.0133 | 1.0127 | 1.0112 | 1.0081 | 1.0075 | 1.0084 | 1.0119 | 1.0125 | 1.0133 | 1.0132 | 1.013 | 1.0126 | 1.0139 | 1.0137 | 1.0137 | 1.014 | 1.015 | 1.0169 | 1.0164 | 1.0158 | 1.0155 | 1.0145 | 1.0129
188 | 1.0142 | 1.0133 | 1.0127 | 1.0112 | 1.0081 | 1.0075 | 1.0084 | 1.0119 | 1.0125 | 1.0133 | 1.0132 | 1.013 | 1.0126 | 1.0139 | 1.0137 | 1.0137 | 1.014 | 1.015 | 1.0169 | 1.0164 | 1.0158 | 1.0155 | 1.0145 | 1.0129
189 | 1.0142 | 1.0133 | 1.0127 | 1.0112 | 1.0081 | 1.0075 | 1.0084 | 1.0119 | 1.0125 | 1.0133 | 1.0132 | 1.013 | 1.0126 | 1.0139 | 1.0137 | 1.0137 | 1.014 | 1.015 | 1.0169 | 1.0164 | 1.0158 | 1.0155 | 1.0145 | 1.0129
191 | 1.022 | 1.0203 | 1.0205 | 1.0181 | 1.0153 | 1.0122 | 1.0272 | 1.0334 | 1.035 | 1.036 | 1.0379 | 1.0417 | 1.0418 | 1.0412 | 1.0423 | 1.0422 | 1.0424 | 1.046 | 1.0458 | 1.0454 | 1.0449 | 1.0459 | 1.0468 | 1.0474
192 | 1.0208 | 1.019 | 1.0192 | 1.017 | 1.0142 | 1.011 | 1.0228 | 1.0284 | 1.0307 | 1.0316 | 1.0331 | 1.0374 | 1.0374 | 1.0366 | 1.0379 | 1.0376 | 1.038 | 1.0413 | 1.0418 | 1.0421 | 1.0415 | 1.042 | 1.0412 | 1.0401
194 | 1.0234 | 1.0223 | 1.0223 | 1.0187 | 1.0152 | 1.0125 | 1.0196 | 1.0284 | 1.031 | 1.0324 | 1.033 | 1.0354 | 1.0353 | 1.0348 | 1.0364 | 1.0365 | 1.0371 | 1.0374 | 1.0375 | 1.0391 | 1.0395 | 1.0417 | 1.0406 | 1.0369
195 | 1.0212 | 1.02 | 1.0194 | 1.017 | 1.013 | 1.0116 | 1.0139 | 1.0193 | 1.0229 | 1.024 | 1.0232 | 1.0212 | 1.0204 | 1.0213 | 1.0218 | 1.0219 | 1.0246 | 1.0295 | 1.0305 | 1.0308 | 1.0282 | 1.0276 | 1.0238 | 1.0215
196 | 1.0361 | 1.0346 | 1.0324 | 1.0268 | 1.02 | 1.0161 | 1.0191 | 1.0284 | 1.0307 | 1.03 | 1.0278 | 1.029 | 1.0275 | 1.0337 | 1.0356 | 1.0362 | 1.034 | 1.0337 | 1.0347 | 1.0399 | 1.0403 | 1.0429 | 1.0442 | 1.0411
198 | 1.0362 | 1.0348 | 1.0295 | 1.0237 | 1.0166 | 1.0164 | 1.0201 | 1.0311 | 1.0335 | 1.0321 | 1.029 | 1.0298 | 1.0283 | 1.0346 | 1.0357 | 1.0363 | 1.0341 | 1.0363 | 1.0375 | 1.0427 | 1.0431 | 1.0455 | 1.0467 | 1.0411
200 | 1.0219 | 1.0201 | 1.0204 | 1.018 | 1.0151 | 1.012 | 1.0257 | 1.0318 | 1.0336 | 1.0346 | 1.0364 | 1.0403 | 1.0404 | 1.0398 | 1.0409 | 1.0408 | 1.041 | 1.0444 | 1.0442 | 1.0438 | 1.0432 | 1.0442 | 1.0445 | 1.0445
201 | 1.0219 | 1.0201 | 1.0204 | 1.018 | 1.0151 | 1.012 | 1.0257 | 1.0318 | 1.0336 | 1.0346 | 1.0364 | 1.0403 | 1.0404 | 1.0398 | 1.0409 | 1.0408 | 1.041 | 1.0444 | 1.0442 | 1.0438 | 1.0432 | 1.0443 | 1.0445 | 1.0445
202 | 1.0219 | 1.0201 | 1.0204 | 1.018 | 1.0151 | 1.012 | 1.0257 | 1.0318 | 1.0336 | 1.0346 | 1.0364 | 1.0403 | 1.0404 | 1.0398 | 1.0409 | 1.0408 | 1.041 | 1.0444 | 1.0442 | 1.0438 | 1.0432 | 1.0443 | 1.0445 | 1.0445
203 | 1.0219 | 1.0201 | 1.0204 | 1.018 | 1.0151 | 1.012 | 1.0257 | 1.0318 | 1.0336 | 1.0346 | 1.0364 | 1.0403 | 1.0404 | 1.0397 | 1.0409 | 1.0407 | 1.041 | 1.0444 | 1.0442 | 1.0438 | 1.0432 | 1.0442 | 1.0445 | 1.0446
206 | 1.0172 | 1.0174 | 1.0181 | 1.0153 | 1.011 | 1.0091 | 1.017 | 1.0261 | 1.0292 | 1.0299 | 1.0306 | 1.0308 | 1.0307 | 1.0288 | 1.0304 | 1.0298 | 1.0306 | 1.0309 | 1.0298 | 1.0295 | 1.0309 | 1.0329 | 1.0303 | 1.0256
207 | 1.0172 | 1.0174 | 1.0181 | 1.0153 | 1.011 | 1.0091 | 1.017 | 1.0261 | 1.0292 | 1.0299 | 1.0306 | 1.0308 | 1.0307 | 1.0288 | 1.0304 | 1.0298 | 1.0306 | 1.031 | 1.0298 | 1.0296 | 1.0309 | 1.0329 | 1.0303 | 1.0256
218 | 1.0187 | 1.0186 | 1.0191 | 1.0162 | 1.012 | 1.0099 | 1.0169 | 1.0257 | 1.0286 | 1.0295 | 1.0303 | 1.0307 | 1.0308 | 1.0296 | 1.0312 | 1.031 | 1.0318 | 1.0319 | 1.031 | 1.0309 | 1.032 | 1.0341 | 1.032 | 1.0278
220 | 1.016 | 1.0164 | 1.0174 | 1.0147 | 1.0105 | 1.0089 | 1.0165 | 1.0254 | 1.0301 | 1.0312 | 1.0319 | 1.0318 | 1.0318 | 1.0307 | 1.0328 | 1.0328 | 1.0338 | 1.0323 | 1.0308 | 1.0305 | 1.0326 | 1.0345 | 1.0307 | 1.0252
222 | 1.0194 | 1.0183 | 1.0171 | 1.0165 | 1.0146 | 1.0151 | 1.0139 | 1.0176 | 1.0199 | 1.0228 | 1.0233 | 1.0239 | 1.0233 | 1.0247 | 1.024 | 1.0237 | 1.0232 | 1.0236 | 1.0243 | 1.024 | 1.0239 | 1.02 | 1.0197 | 1.0194
225 | 1.0329 | 1.035 | 1.0352 | 1.0331 | 1.0282 | 1.023 | 1.0315 | 1.0409 | 1.0428 | 1.0435 | 1.0453 | 1.0462 | 1.0463 | 1.0452 | 1.0466 | 1.0462 | 1.0465 | 1.0472 | 1.0478 | 1.0483 | 1.0481 | 1.0483 | 1.0484 | 1.0481
227 | 1.0408 | 1.035 | 1.0314 | 1.0348 | 1.0391 | 1.0382 | 1.0354 | 1.0406 | 1.0397 | 1.0416 | 1.0402 | 1.0405 | 1.0404 | 1.0404 | 1.0406 | 1.0406 | 1.0406 | 1.0434 | 1.0443 | 1.0451 | 1.0448 | 1.042 | 1.0402 | 1.0397
228 | 1.0408 | 1.0349 | 1.0313 | 1.0348 | 1.0391 | 1.0382 | 1.0355 | 1.0406 | 1.0397 | 1.0416 | 1.0403 | 1.0406 | 1.0404 | 1.0404 | 1.0407 | 1.0407 | 1.0407 | 1.0434 | 1.0443 | 1.0451 | 1.0448 | 1.042 | 1.0403 | 1.0398
229 | 1.0325 | 1.0354 | 1.0372 | 1.035 | 1.0279 | 1.0207 | 1.0289 | 1.041 | 1.0422 | 1.0418 | 1.0424 | 1.0392 | 1.0386 | 1.0373 | 1.0397 | 1.0398 | 1.0419 | 1.044 | 1.0407 | 1.0385 | 1.0396 | 1.0416 | 1.0416 | 1.0394
230 | 1.0325 | 1.0354 | 1.0372 | 1.035 | 1.0279 | 1.0207 | 1.0291 | 1.0413 | 1.0425 | 1.0422 | 1.0428 | 1.0395 | 1.0388 | 1.0373 | 1.0397 | 1.0398 | 1.0419 | 1.0444 | 1.0408 | 1.0385 | 1.0396 | 1.0417 | 1.0416 | 1.0395
231 | 1.0325 | 1.0338 | 1.0324 | 1.0305 | 1.0274 | 1.0225 | 1.0297 | 1.0419 | 1.0428 | 1.0425 | 1.0427 | 1.0429 | 1.0428 | 1.0404 | 1.0421 | 1.0421 | 1.0443 | 1.0441 | 1.0436 | 1.043 | 1.0437 | 1.0473 | 1.0445 | 1.0422
232 | 1.0374 | 1.0408 | 1.0424 | 1.0406 | 1.0328 | 1.0231 | 1.0296 | 1.0421 | 1.0433 | 1.0429 | 1.0432 | 1.0405 | 1.0397 | 1.0404 | 1.0435 | 1.0437 | 1.0457 | 1.0458 | 1.0445 | 1.0424 | 1.0436 | 1.0457 | 1.047 | 1.0445
233 | 1.0374 | 1.0408 | 1.0424 | 1.0406 | 1.0328 | 1.0231 | 1.0296 | 1.0421 | 1.0433 | 1.0429 | 1.0432 | 1.0405 | 1.0397 | 1.0404 | 1.0435 | 1.0437 | 1.0457 | 1.0458 | 1.0445 | 1.0424 | 1.0436 | 1.0457 | 1.047 | 1.0445
234 | 1.041 | 1.039 | 1.0387 | 1.039 | 1.0387 | 1.0385 | 1.0379 | 1.0448 | 1.044 | 1.0443 | 1.0434 | 1.0429 | 1.0427 | 1.0424 | 1.0427 | 1.0427 | 1.0428 | 1.0458 | 1.0456 | 1.0456 | 1.0455 | 1.0443 | 1.0425 | 1.0414
235 | 1.041 | 1.0391 | 1.0387 | 1.0391 | 1.0387 | 1.0385 | 1.0379 | 1.0448 | 1.044 | 1.0443 | 1.0434 | 1.0429 | 1.0427 | 1.0424 | 1.0427 | 1.0427 | 1.0428 | 1.0458 | 1.0457 | 1.0456 | 1.0455 | 1.0443 | 1.0425 | 1.0414
236 | 1.041 | 1.0391 | 1.0387 | 1.0391 | 1.0387 | 1.0385 | 1.0379 | 1.0448 | 1.044 | 1.0443 | 1.0434 | 1.0429 | 1.0427 | 1.0424 | 1.0427 | 1.0427 | 1.0428 | 1.0458 | 1.0457 | 1.0456 | 1.0455 | 1.0443 | 1.0425 | 1.0414
237 | 1.04 | 1.0356 | 1.0349 | 1.0335 | 1.0317 | 1.0325 | 1.035 | 1.0446 | 1.0454 | 1.0448 | 1.0451 | 1.0445 | 1.0441 | 1.0428 | 1.044 | 1.0439 | 1.0447 | 1.0461 | 1.0457 | 1.0453 | 1.0459 | 1.0473 | 1.0466 | 1.0426
238 | 1.04 | 1.0356 | 1.0349 | 1.0335 | 1.0317 | 1.0325 | 1.035 | 1.0446 | 1.0454 | 1.0448 | 1.0451 | 1.0445 | 1.0441 | 1.0428 | 1.044 | 1.0439 | 1.0447 | 1.0461 | 1.0457 | 1.0453 | 1.0459 | 1.0473 | 1.0466 | 1.0426
239 | 1.0426 | 1.0411 | 1.0416 | 1.0413 | 1.0389 | 1.0384 | 1.0388 | 1.0455 | 1.0439 | 1.0431 | 1.0428 | 1.0426 | 1.0426 | 1.0421 | 1.0428 | 1.0429 | 1.0428 | 1.0431 | 1.0429 | 1.0414 | 1.0423 | 1.0427 | 1.0423 | 1.0417
240 | 1.0426 | 1.0412 | 1.0416 | 1.0413 | 1.0389 | 1.0384 | 1.0388 | 1.0455 | 1.0439 | 1.0431 | 1.0429 | 1.0426 | 1.0426 | 1.0422 | 1.0428 | 1.0429 | 1.0428 | 1.0431 | 1.0429 | 1.0414 | 1.0423 | 1.0427 | 1.0423 | 1.0417
241 | 1.0359 | 1.0344 | 1.0346 | 1.033 | 1.0298 | 1.028 | 1.0316 | 1.0445 | 1.0453 | 1.0444 | 1.0449 | 1.044 | 1.0435 | 1.0414 | 1.0427 | 1.043 | 1.0441 | 1.0461 | 1.0453 | 1.0438 | 1.0451 | 1.0469 | 1.0447 | 1.0405
242 | 1.0355 | 1.0337 | 1.0339 | 1.0323 | 1.0291 | 1.0275 | 1.0311 | 1.0444 | 1.0451 | 1.0443 | 1.0447 | 1.0438 | 1.0433 | 1.0412 | 1.0425 | 1.0428 | 1.044 | 1.046 | 1.0452 | 1.0436 | 1.045 | 1.0468 | 1.0454 | 1.0405
243 | 1.04 | 1.0356 | 1.0349 | 1.0335 | 1.0317 | 1.0325 | 1.035 | 1.0446 | 1.0454 | 1.0448 | 1.0451 | 1.0445 | 1.0441 | 1.0428 | 1.044 | 1.0439 | 1.0447 | 1.0461 | 1.0457 | 1.0453 | 1.0459 | 1.0473 | 1.0466 | 1.0426
244 | 1.04 | 1.0356 | 1.0349 | 1.0335 | 1.0317 | 1.0325 | 1.035 | 1.0446 | 1.0454 | 1.0448 | 1.0451 | 1.0445 | 1.0441 | 1.0428 | 1.044 | 1.0439 | 1.0447 | 1.0461 | 1.0457 | 1.0453 | 1.0459 | 1.0473 | 1.0466 | 1.0426
250 | 1.0318 | 1.0305 | 1.0302 | 1.03 | 1.0282 | 1.0296 | 1.0358 | 1.0414 | 1.0413 | 1.0398 | 1.0382 | 1.0376 | 1.0375 | 1.037 | 1.0375 | 1.0376 | 1.0378 | 1.0429 | 1.0427 | 1.0407 | 1.0407 | 1.0398 | 1.0381 | 1.0353
251 | 1.0166 | 1.0169 | 1.0165 | 1.0149 | 1.0127 | 1.0119 | 1.0278 | 1.0296 | 1.0299 | 1.0294 | 1.0289 | 1.0259 | 1.0251 | 1.0246 | 1.0228 | 1.0229 | 1.0251 | 1.0276 | 1.029 | 1.0261 | 1.0252 | 1.0234 | 1.0197 | 1.0165
252 | 1.029 | 1.0285 | 1.0279 | 1.0259 | 1.0219 | 1.0207 | 1.0221 | 1.025 | 1.0279 | 1.0273 | 1.027 | 1.0289 | 1.0288 | 1.0277 | 1.0282 | 1.0271 | 1.024 | 1.0261 | 1.0323 | 1.0305 | 1.0304 | 1.029 | 1.0282 | 1.022
253 | 1.0264 | 1.0264 | 1.0258 | 1.0234 | 1.0191 | 1.0176 | 1.0194 | 1.0227 | 1.025 | 1.0243 | 1.0237 | 1.0249 | 1.025 | 1.0243 | 1.0249 | 1.0237 | 1.0211 | 1.0236 | 1.0289 | 1.0275 | 1.0274 | 1.0264 | 1.026 | 1.0198
254 | 1.0239 | 1.0239 | 1.0238 | 1.0217 | 1.019 | 1.0181 | 1.035 | 1.0373 | 1.0377 | 1.0371 | 1.0363 | 1.0323 | 1.031 | 1.0303 | 1.0285 | 1.0286 | 1.0312 | 1.0345 | 1.0361 | 1.0327 | 1.0318 | 1.0298 | 1.0258 | 1.0223
255 | 1.031 | 1.03 | 1.0297 | 1.0294 | 1.0277 | 1.029 | 1.0351 | 1.041 | 1.0405 | 1.039 | 1.0373 | 1.0367 | 1.0366 | 1.0361 | 1.0366 | 1.0367 | 1.0369 | 1.0419 | 1.0417 | 1.0398 | 1.0397 | 1.0389 | 1.0373 | 1.0347
262 | 1.0264 | 1.0248 | 1.024 | 1.0211 | 1.0165 | 1.0146 | 1.0164 | 1.0213 | 1.0233 | 1.0231 | 1.0219 | 1.0211 | 1.0197 | 1.0209 | 1.0216 | 1.0217 | 1.0224 | 1.0246 | 1.0252 | 1.0261 | 1.0253 | 1.0265 | 1.0257 | 1.0229
263 | 1.0303 | 1.0285 | 1.0276 | 1.0244 | 1.0196 | 1.0174 | 1.0178 | 1.0218 | 1.0233 | 1.0224 | 1.0212 | 1.0226 | 1.0208 | 1.0232 | 1.0239 | 1.0244 | 1.0227 | 1.0221 | 1.0239 | 1.0256 | 1.0255 | 1.0272 | 1.0282 | 1.0261
264 | 1.0187 | 1.0187 | 1.0196 | 1.0167 | 1.0125 | 1.0102 | 1.0183 | 1.0262 | 1.029 | 1.0294 | 1.0296 | 1.0296 | 1.0294 | 1.0281 | 1.0298 | 1.0298 | 1.0309 | 1.0302 | 1.0292 | 1.029 | 1.0304 | 1.0324 | 1.0305 | 1.0262
265 | 1.0247 | 1.0232 | 1.0224 | 1.0195 | 1.0151 | 1.0132 | 1.0151 | 1.0202 | 1.0222 | 1.0222 | 1.0212 | 1.0204 | 1.0192 | 1.0205 | 1.0211 | 1.0213 | 1.022 | 1.0241 | 1.0247 | 1.0256 | 1.0247 | 1.0259 | 1.0249 | 1.0222
266 | 1.0298 | 1.028 | 1.0271 | 1.0239 | 1.0191 | 1.0169 | 1.0173 | 1.0215 | 1.023 | 1.0222 | 1.021 | 1.0225 | 1.0208 | 1.0233 | 1.024 | 1.0245 | 1.0227 | 1.0222 | 1.0239 | 1.0256 | 1.0255 | 1.0272 | 1.0282 | 1.0261
267 | 1.0211 | 1.0207 | 1.0213 | 1.0184 | 1.0146 | 1.0119 | 1.0199 | 1.0254 | 1.0278 | 1.0281 | 1.0286 | 1.0296 | 1.0292 | 1.0279 | 1.0295 | 1.0293 | 1.0301 | 1.0295 | 1.0296 | 1.0305 | 1.0311 | 1.0328 | 1.0316 | 1.0286
268 | 1.0319 | 1.0331 | 1.0329 | 1.0311 | 1.0266 | 1.0218 | 1.029 | 1.0403 | 1.0417 | 1.0413 | 1.0418 | 1.0417 | 1.0415 | 1.04 | 1.0418 | 1.0417 | 1.0432 | 1.0436 | 1.0433 | 1.0431 | 1.0437 | 1.0456 | 1.0446 | 1.0421
273 | 1.0125 | 1.0118 | 1.0127 | 1.0109 | 1.0086 | 1.0085 | 1.0114 | 1.0168 | 1.0199 | 1.0217 | 1.0225 | 1.0233 | 1.0254 | 1.0265 | 1.027 | 1.0274 | 1.0285 | 1.0273 | 1.0283 | 1.0312 | 1.0349 | 1.0291 | 1.0252 | 1.0228
293 | 1.0068 | 1.0076 | 1.0076 | 1.0086 | 1.0069 | 1.0068 | 1.0144 | 1.0132 | 1.0132 | 1.0127 | 1.0124 | 1.0129 | 1.0123 | 1.012 | 1.0104 | 1.0105 | 1.0128 | 1.0116 | 1.0127 | 1.0122 | 1.0119 | 1.0112 | 1.0099 | 1.0088

## Transf Tap Ratio
fbus | tbus \ Hour | 00:00 - 01:00 | 01:00 - 02:00 | 02:00 - 03:00 | 03:00 - 04:00 | 04:00 - 05:00 | 05:00 - 06:00 | 06:00 - 07:00 | 07:00 - 08:00 | 08:00 - 09:00 | 09:00 - 10:00 | 10:00 - 11:00 | 11:00 - 12:00 | 12:00 - 13:00 | 13:00 - 14:00 | 14:00 - 15:00 | 15:00 - 16:00 | 16:00 - 17:00 | 17:00 - 18:00 | 18:00 - 19:00 | 19:00 - 20:00 | 20:00 - 21:00 | 21:00 - 22:00 | 22:00 - 23:00 | 23:00 - 00:00
8 | 36 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167
8 | 109 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333
9 | 112 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
9 | 112 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
9 | 112 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
9 | 112 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
10 | 80 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.99167 | 0.99583 | 0.99583 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 0.99583
10 | 80 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.99167 | 0.99583 | 0.99583 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 0.99583
10 | 113 | 1.0042 | 1.0042 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
10 | 113 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0042
10 | 113 | 1.0042 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
11 | 117 | 1 | 1 | 1.0042 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1.0042 | 1
11 | 117 | 1 | 1 | 1.0042 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1.0042 | 1.0042 | 1.0042
12 | 121 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1
12 | 121 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1
12 | 121 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1
12 | 121 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1
13 | 84 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167
13 | 123 | 0.99583 | 0.99583 | 1 | 1 | 0.99583 | 0.99583 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
13 | 123 | 0.99583 | 0.99583 | 1 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583
13 | 123 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583
13 | 123 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583
14 | 86 | 0.9875 | 0.9875 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167
14 | 86 | 0.9875 | 0.9875 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167
15 | 87 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
15 | 87 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
15 | 126 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083
15 | 126 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
15 | 126 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
16 | 47 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.98333 | 0.98333 | 0.98333 | 0.97917 | 0.98333 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.99167 | 0.98333
17 | 88 | 0.98333 | 0.98333 | 0.97917 | 0.97917 | 0.98333 | 0.99167 | 1 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.98333 | 0.97917
17 | 88 | 0.98333 | 0.98333 | 0.97917 | 0.97917 | 0.98333 | 0.99167 | 1 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.98333 | 0.97917
17 | 128 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875
17 | 128 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875
18 | 133 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0167 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0208 | 1.0208 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0125
18 | 133 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0167 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0208 | 1.0208 | 1.0167 | 1.0167 | 1.0167 | 1.0125 | 1.0125
18 | 133 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0167 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0208 | 1.0208 | 1.0167 | 1.0167 | 1.0167 | 1.0125 | 1.0125
19 | 140 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167
19 | 140 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167
19 | 140 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167
20 | 141 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583
20 | 141 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583
21 | 142 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
21 | 142 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
22 | 146 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125
23 | 149 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.99167
23 | 149 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.99167
23 | 149 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583
24 | 98 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875
24 | 98 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875
24 | 150 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1
24 | 150 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1
25 | 151 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167
25 | 151 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.99167
25 | 151 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167
29 | 102 | 0.98333 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.97917 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875
29 | 159 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083
29 | 159 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083
31 | 72 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.99167 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875
31 | 72 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.9875
31 | 162 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
31 | 162 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042
32 | 104 | 0.98333 | 0.97917 | 0.97917 | 0.97917 | 0.98333 | 0.99167 | 1 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99583 | 0.99583 | 0.99167 | 0.9875 | 0.98333 | 0.97917
32 | 104 | 0.98333 | 0.97917 | 0.97917 | 0.97917 | 0.98333 | 0.99167 | 1 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99583 | 0.99583 | 0.99167 | 0.9875 | 0.98333 | 0.97917
32 | 108 | 1.0083 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0125 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0167 | 1.0167 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083
33 | 163 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0042
33 | 163 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0042
34 | 107 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1.0042 | 1.0042 | 0.99583 | 1 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042
34 | 107 | 1 | 1 | 1 | 1 | 0.99583 | 1 | 1 | 0.99167 | 0.99583 | 1 | 1 | 1.0042 | 1.0042 | 1 | 1.0042 | 1.0042 | 1.0042 | 0.99583 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1
34 | 169 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125
34 | 169 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125
35 | 171 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167
35 | 171 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167
36 | 109 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.98333 | 0.9875 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.9875
36 | 109 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.9875 | 0.9875
37 | 110 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1
37 | 110 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1
37 | 110 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583
38 | 111 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
38 | 111 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
38 | 111 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
39 | 114 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1
39 | 114 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
39 | 114 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
40 | 115 | 1.0167 | 1.0167 | 1.0167 | 1.0125 | 1.0125 | 1.0083 | 1.0125 | 1.0167 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.025 | 1.025 | 1.025 | 1.025 | 1.0292 | 1.025 | 1.025
40 | 115 | 1.0125 | 1.0125 | 1.0167 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.025 | 1.0208 | 1.025 | 1.0208 | 1.0208
41 | 81 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333
41 | 81 | 0.98333 | 0.98333 | 0.97917 | 0.97917 | 0.98333 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333
41 | 116 | 0.99583 | 0.99583 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1
41 | 116 | 0.99583 | 0.99583 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1
42 | 118 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
42 | 118 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
42 | 118 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
42 | 118 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
43 | 82 | 0.96667 | 0.96667 | 0.9625 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.9625 | 0.96667 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.975 | 0.97083 | 0.97083 | 0.97083 | 0.97083
43 | 82 | 0.9625 | 0.9625 | 0.9625 | 0.9625 | 0.9625 | 0.9625 | 0.9625 | 0.95833 | 0.9625 | 0.96667 | 0.96667 | 0.97083 | 0.96667 | 0.97083 | 0.97083 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.97083 | 0.97083 | 0.97083 | 0.96667 | 0.96667
43 | 119 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.97917 | 0.97917 | 0.97917 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333
44 | 120 | 0.99583 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
44 | 120 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
44 | 120 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
44 | 120 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
45 | 85 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.97917 | 0.97917 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.97917 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333
45 | 85 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.97917 | 0.97917 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.97917 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333
45 | 124 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1
45 | 124 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
45 | 124 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1
46 | 125 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583
46 | 125 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
46 | 125 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1
47 | 127 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
47 | 127 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1
47 | 127 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
48 | 129 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.99167 | 0.98333 | 0.9875
48 | 129 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.99167 | 0.98333 | 0.9875
48 | 129 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333
49 | 130 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99583 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 1 | 0.99583 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 0.99583
49 | 130 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1
49 | 130 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1
49 | 130 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99583 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1
50 | 89 | 0.9625 | 0.9625 | 0.9625 | 0.95833 | 0.9625 | 0.9625 | 0.9625 | 0.95833 | 0.9625 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.96667 | 0.96667
50 | 89 | 0.96667 | 0.96667 | 0.9625 | 0.9625 | 0.9625 | 0.96667 | 0.96667 | 0.9625 | 0.96667 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.975 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.975 | 0.97083 | 0.975 | 0.97083 | 0.97083
50 | 89 | 0.96667 | 0.96667 | 0.9625 | 0.9625 | 0.9625 | 0.96667 | 0.96667 | 0.9625 | 0.96667 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.97083 | 0.975 | 0.97083 | 0.97083 | 0.97083 | 0.97083
51 | 90 | 0.98333 | 0.97917 | 0.97917 | 0.975 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.97917 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333
52 | 132 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083
53 | 134 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
53 | 134 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042
53 | 134 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
55 | 135 | 0.99583 | 0.99583 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583
55 | 135 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583
55 | 135 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583
55 | 135 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583
56 | 136 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99583
56 | 136 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99583
56 | 136 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99583
57 | 93 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333
57 | 93 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333
57 | 138 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1.0042 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1
57 | 138 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
57 | 138 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1
58 | 139 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1
58 | 139 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1
58 | 139 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1
59 | 143 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
59 | 143 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
60 | 144 | 1 | 1 | 1.0042 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
60 | 144 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0042
62 | 152 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042
62 | 152 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
62 | 152 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
63 | 153 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125
63 | 153 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0167 | 1.0167 | 1.0125
64 | 154 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
64 | 154 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583
65 | 155 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083
65 | 155 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083
65 | 155 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083
66 | 156 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0083 | 1.0083
66 | 156 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 1 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083
68 | 157 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 1 | 1 | 1.0042 | 1 | 1 | 1 | 1.0042 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042
68 | 157 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 1 | 1 | 1.0042 | 1 | 1 | 1 | 1.0042 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042
69 | 101 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.97917 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.9875
71 | 161 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042
71 | 161 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042
73 | 165 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0125 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0208 | 1.0167
73 | 165 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0125 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0208 | 1.0167 | 1.0208 | 1.0208 | 1.0208
74 | 166 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 0.99583
74 | 166 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 0.99583
75 | 167 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0167 | 1.0167 | 1.0167 | 1.0125 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167
75 | 167 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0167
75 | 167 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0167
76 | 168 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167
76 | 168 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.99167 | 0.99167
76 | 168 | 0.99583 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99167 | 0.99583 | 0.99583
77 | 106 | 0.98333 | 0.97917 | 0.97917 | 0.97917 | 0.98333 | 0.98333 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875
77 | 106 | 0.98333 | 0.97917 | 0.97917 | 0.97917 | 0.98333 | 0.98333 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875
77 | 106 | 0.98333 | 0.97917 | 0.97917 | 0.97917 | 0.98333 | 0.98333 | 0.9875 | 0.98333 | 0.98333 | 0.98333 | 0.98333 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875 | 0.9875
78 | 170 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083
78 | 170 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083
79 | 172 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0042 | 1.0125 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0208 | 1.0208 | 1.0167
79 | 172 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0167
81 | 116 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0042 | 1.0083 | 1.0167 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0042 | 1.0083 | 1.0125 | 1.0125 | 1.0125
81 | 116 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0042 | 1.0083 | 1.0167 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0042 | 1.0083 | 1.0125 | 1.0125 | 1.0125
82 | 119 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0083 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1.0042
82 | 119 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0083 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1.0042
82 | 119 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0083 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1.0042
83 | 122 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1
83 | 122 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1
83 | 122 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0042 | 1 | 1 | 1 | 1.0042 | 1.0042 | 1
88 | 128 | 1 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1 | 0.99583 | 1.0042 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 1 | 1.0042 | 1.0042
88 | 128 | 1 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1 | 0.99583 | 1.0042 | 1 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 0.99583 | 1 | 1 | 1 | 1 | 0.99583 | 0.99583 | 0.99583 | 1 | 1.0042 | 1.0042
89 | 131 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
89 | 131 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042
89 | 131 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083 | 1.0083
92 | 137 | 1.0042 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1 | 1.0042 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083
92 | 137 | 1.0042 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1 | 1.0042 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083
95 | 145 | 1.0208 | 1.0208 | 1.0208 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.025 | 1.025 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.025 | 1.0208
95 | 145 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0208 | 1.0208 | 1.0167
95 | 145 | 1.0167 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0208 | 1.0208 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0167 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0208 | 1.0167
97 | 147 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0083 | 1.0083
101 | 158 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0083
101 | 158 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0125 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0083
103 | 160 | 1.0083 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0167 | 1.0167 | 1.0125
103 | 160 | 1.0083 | 1.0083 | 1.0083 | 1.0042 | 1.0042 | 1.0042 | 1.0042 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0167 | 1.0167 | 1.0125
105 | 164 | 1.0125 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0167 | 1.0167 | 1.0167 | 1.0125 | 1.0125 | 1.0125
105 | 164 | 1.0125 | 1.0083 | 1.0083 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0125 | 1.0167 | 1.0167 | 1.0167 | 1.0125 | 1.0125 | 1.0125

## Transf Data
fbus | tbus | Manufacture year | Commissioning year | Annual maximum loading [MVA] | Voltage ratio [kV] | Insulation medium | Cooling system | Transformer type | Indoor/Outdoor | Criticallity indicator | Time over rating 50% [%] | Clients affected [MVA] | ENS in fault [MWh] | Mean load [%] | Value of lost load [k€/MWh]
8 | 36 | 2016 | 2018 | 69.9 | 220/150 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 18.1 | Between 2 and 5
8 | 109 | 2001 | 2003 | 54 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 42.295 | 0 | 24.9 | Between 2 and 5
9 | 112 | 2007 | 2007 | 36.5 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 26.325 | 0 | 20.9 | Between 2 and 5
9 | 112 | 2004 | 2005 | 36 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 25.665 | 0 | 20.4 | Between 2 and 5
9 | 112 | 2010 | 2010 | 35 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 24.925 | 0 | 19.8 | Between 2 and 5
9 | 112 | 1978 | 1978 | 34.1 | 150/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 24.12 | 0 | 20.1 | Between 2 and 5
10 | 80 | 1999 | 2009 | 81.7 | 400/150 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 19.2 | Between 2 and 5
10 | 80 | 2002 | 2002 | 82 | 400/150 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 19.2 | Between 2 and 5
10 | 113 | 1981 | 1983 | 17 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 12.635 | 0 | 25.3 | Between 2 and 5
10 | 113 | 1974 | 2005 | 23.2 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 17.485 | 0 | 27.8 | Between 2 and 5
10 | 113 | 2011 | 2011 | 40.2 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 30.26 | 0 | 24 | Between 2 and 5
11 | 117 | 2016 | 2016 | 29.4 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 20.11 | 0 | 16 | Between 2 and 5
11 | 117 | 1996 | 2016 | 30.8 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 20.93 | 0 | 16.6 | Between 2 and 5
12 | 121 | 1991 | 1991 | 50.7 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 39.705 | 0 | 31.5 | Between 2 and 5
12 | 121 | 2003 | 2004 | 38.2 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 29.95 | 0 | 23.8 | Between 2 and 5
12 | 121 | 1982 | 1983 | 23.2 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 18.045 | 0 | 28.6 | Between 2 and 5
12 | 121 | 1993 | 2015 | 38.6 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 29.4 | 0 | 23.3 | Between 2 and 5
13 | 84 | 2003 | 2014 | 212.7 | 400/150 | Oil | ONAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 28.9 | Between 2 and 5
13 | 123 | 1975 | 1980 | 49.2 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 27.74 | 0 | 22 | Between 2 and 5
13 | 123 | 1975 | 1980 | 50.5 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 28.495 | 0 | 22.6 | Between 2 and 5
13 | 123 | 1992 | 1992 | 48.5 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 27.515 | 0 | 21.8 | Between 2 and 5
13 | 123 | 2011 | 2011 | 48.5 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 27.5 | 0 | 21.8 | Between 2 and 5
14 | 86 | 1977 | 1979 | 162.8 | 400/150 | Oil | ODAF | Autotransformer (3 single-phase units) | Outdoor | C | 0 | - | 0 | 23.1 | Between 2 and 5
14 | 86 | 1977 | 1981 | 162.6 | 400/150 | Oil | ODAF | Autotransformer (3 single-phase units) | Outdoor | C | 0 | - | 0 | 23 | Between 2 and 5
15 | 87 | 1985 | 1986 | 67.4 | 400/150 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 10.4 | Between 2 and 5
15 | 87 | 1993 | 1994 | 68.4 | 400/150 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 10.5 | Between 2 and 5
15 | 126 | 2017 | 2019 | 54.3 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 44.525 | 0 | 35.3 | Between 2 and 5
15 | 126 | 1978 | 1980 | 19.7 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 15.59 | 0 | 13 | Between 2 and 5
15 | 126 | 1978 | 1981 | 19.7 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 15.66 | 0 | 13.1 | Between 2 and 5
16 | 47 | 2011 | 2011 | 54.9 | 220/150 | Oil | ONAF | Autotransformer (1 three-phase unit) | Outdoor | C | 15 | - | 0 | 11 | Between 2 and 5
17 | 88 | 1987 | 1988 | 70.1 | 400/150 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 12.4 | Between 2 and 5
17 | 88 | 1986 | 1987 | 70.1 | 400/150 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 12.4 | Between 2 and 5
17 | 128 | 1982 | 1984 | 71.9 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 15 | 51.11 | 0 | 42.6 | Between 2 and 5
17 | 128 | 1980 | 1980 | 71.1 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 15 | 50.565 | 0 | 40.1 | Between 2 and 5
18 | 133 | 2004 | 2005 | 28.6 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 17.23 | 0 | 10.1 | Between 2 and 5
18 | 133 | 1986 | 1987 | 26.5 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 15.9 | 0 | 12.7 | Between 2 and 5
18 | 133 | 1986 | 1987 | 26.5 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 15.58 | 0 | 12.4 | Between 2 and 5
19 | 140 | 1968 | 1999 | 34.8 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 15 | 20.94 | 0 | 33.2 | Between 2 and 5
19 | 140 | 1985 | 1986 | 29.1 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 17.485 | 0 | 27.7 | Between 2 and 5
19 | 140 | 1976 | 1992 | 32.4 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 15 | 19.465 | 0 | 30.9 | Between 2 and 5
20 | 141 | 2005 | 2008 | 60.9 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 34.745 | 0 | 20.4 | Between 2 and 5
20 | 141 | 2007 | 2007 | 60.4 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 34.45 | 0 | 20.3 | Between 2 and 5
21 | 142 | 2014 | 2014 | 67.2 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 31.505 | 0 | 18.5 | Between 2 and 5
21 | 142 | 2007 | 2015 | 72.5 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 33.93 | 0 | 20 | Between 2 and 5
22 | 146 | 2016 | 2017 | 16.3 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | A | 0 | 7.885 | 16 | 6.3 | Between 2 and 5
23 | 149 | 2006 | 2007 | 54.7 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 38.115 | 0 | 30.3 | Between 2 and 5
23 | 149 | 1995 | 1995 | 53.9 | 150/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 37.49 | 0 | 29.8 | Between 2 and 5
23 | 149 | 1992 | 1992 | 53.2 | 150/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 36.57 | 0 | 29 | Between 2 and 5
24 | 98 | 2005 | 2006 | 86.3 | 400/150 | Oil | ODAF | Phase-shifting autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 11.6 | Between 2 and 5
24 | 98 | 2009 | 2009 | 88.2 | 400/150 | Oil | ODAF | Phase-shifting autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 11.8 | Between 2 and 5
24 | 150 | 1982 | 2004 | 20.7 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 8.74 | 0 | 13.9 | Between 2 and 5
24 | 150 | 1982 | 1992 | 15.7 | 150/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 6.635 | 0 | 10.5 | Between 2 and 5
25 | 151 | 1993 | 1996 | 74.7 | 150/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 30 | 50.345 | 0 | 40 | Between 2 and 5
25 | 151 | 1996 | 1996 | 77.8 | 150/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 30 | 52.225 | 0 | 41.4 | Between 2 and 5
25 | 151 | 2007 | 2007 | 82.2 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 54.86 | 0 | 32.3 | Between 2 and 5
29 | 102 | 2009 | 2009 | 108.2 | 400/150 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 16.3 | Between 2 and 5
29 | 159 | 2008 | 2008 | 45.6 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 24.185 | 0 | 14.2 | Between 2 and 5
29 | 159 | 2004 | 2006 | 43.5 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 23.085 | 0 | 13.6 | Between 2 and 5
31 | 72 | 2007 | 2007 | 61.4 | 220/150 | Oil | ONAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 18.3 | Between 2 and 5
31 | 72 | 2010 | 2011 | 56.9 | 220/150 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 17 | Between 2 and 5
31 | 162 | 1986 | 2007 | 17.3 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 9.15 | 0 | 14.5 | Between 2 and 5
31 | 162 | 2009 | 2010 | 28.9 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 15.405 | 0 | 12.2 | Between 2 and 5
32 | 104 | 2008 | 2008 | 118.5 | 400/150 | Oil | ODAF | Phase-shifting autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 15.2 | Between 2 and 5
32 | 104 | 2008 | 2008 | 118.5 | 400/150 | Oil | ODAF | Phase-shifting autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 15.2 | Between 2 and 5
32 | 108 | 2009 | 2009 | 26.1 | 150/130 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | A | 0 | - | 11.8 | 8.1 | Between 2 and 5
33 | 163 | 2008 | 2008 | 94 | 150/63 | Oil | ONAF | Transformer (3 single-phase units) | Outdoor | C | 10 | 33.935 | 0 | 19.9 | Between 2 and 5
33 | 163 | 2011 | 2011 | 94 | 150/63 | Oil | ONAF | Transformer (3 single-phase units) | Outdoor | C | 10 | 33.91 | 0 | 19.9 | Between 2 and 5
34 | 107 | 2010 | 2011 | 79.4 | 400/150 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 12 | Between 2 and 5
34 | 107 | 2016 | 2017 | 61.9 | 400/150 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 10.3 | Between 2 and 5
34 | 169 | 2010 | 2011 | 18.9 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 9.165 | 0 | 7.3 | Between 2 and 5
34 | 169 | 2011 | 2011 | 18.8 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 9.09 | 0 | 7.2 | Between 2 and 5
35 | 171 | 1974 | 2009 | 32.8 | 150/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | B | 15 | 21.205 | 0 | 33.7 | Between 2 and 5
35 | 171 | 1972 | 2014 | 34.7 | 150/63 | Oil | ONAN | Transformer (1 three-phase unit) | Outdoor | B | 15 | 22.05 | 0 | 35 | Between 2 and 5
36 | 109 | 2003 | 2003 | 61.9 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 46.66 | 0 | 27.4 | Between 2 and 5
36 | 109 | 2009 | 2009 | 60.9 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 46.125 | 0 | 27.1 | Between 2 and 5
37 | 110 | 1997 | 1998 | 62.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 42.87 | 0 | 25.2 | Between 2 and 5
37 | 110 | 2002 | 2002 | 62.1 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 42.63 | 0 | 25.1 | Between 2 and 5
37 | 110 | 2009 | 2009 | 54.6 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 37.485 | 0 | 22 | Between 2 and 5
38 | 111 | 2010 | 2011 | 58.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 37.715 | 0 | 22.2 | Between 2 and 5
38 | 111 | 2011 | 2011 | 58.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 37.715 | 0 | 22.2 | Between 2 and 5
38 | 111 | 2010 | 2011 | 58.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 37.675 | 0 | 22.2 | Between 2 and 5
39 | 114 | 1981 | 1982 | 53.8 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 32.48 | 0 | 25.8 | Between 2 and 5
39 | 114 | 2015 | 2015 | 47.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 29.425 | 0 | 17.3 | Between 2 and 5
39 | 114 | 2006 | 2009 | 50.9 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 30.385 | 0 | 24.1 | Between 2 and 5
40 | 115 | 1973 | 2014 | 19 | 220/63 | Oil | ONAF | Transformer (3 single-phase units) | Outdoor | C | 0 | 8.89 | 0 | 7.4 | Between 2 and 5
40 | 115 | 2016 | 2016 | 16.5 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 7.98 | 0 | 6.3 | Between 2 and 5
41 | 81 | 2014 | 2014 | 74.8 | 400/220 | Oil | ONAF | Autotransformer (1 three-phase unit) | Indoor | C | 0 | - | 0 | 6.9 | Between 2 and 5
41 | 81 | 2011 | 2013 | 74.5 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Indoor | C | 0 | - | 0 | 6.9 | Between 2 and 5
41 | 116 | 2008 | 2008 | 67.6 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 51.32 | 0 | 30.2 | Between 2 and 5
41 | 116 | 2007 | 2007 | 66.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 50.44 | 0 | 29.7 | Between 2 and 5
42 | 118 | 1989 | 2003 | 23.7 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 17.29 | 0 | 13.7 | Between 2 and 5
42 | 118 | 1983 | 2016 | 11.8 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 8.61 | 0 | 13.7 | Between 2 and 5
42 | 118 | 1992 | 2016 | 11.5 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 8.36 | 0 | 13.3 | Between 2 and 5
42 | 118 | 1983 | 2002 | 22.1 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 16.11 | 0 | 12.8 | Between 2 and 5
43 | 82 | 2002 | 2003 | 205.5 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 34.4 | Between 2 and 5
43 | 82 | 2008 | 2008 | 157.6 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 26 | Between 2 and 5
43 | 119 | 2011 | 2012 | 25.6 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 17.885 | 0 | 10.5 | Between 2 and 5
44 | 120 | 2007 | 2008 | 51.1 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 37.145 | 0 | 21.8 | Between 2 and 5
44 | 120 | 1982 | 1983 | 55.6 | 220/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 39.815 | 0 | 31.6 | Between 2 and 5
44 | 120 | 1994 | 1994 | 54.8 | 220/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 39.48 | 0 | 31.3 | Between 2 and 5
44 | 120 | 1993 | 1994 | 52.5 | 220/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 38.57 | 0 | 30.6 | Between 2 and 5
45 | 85 | 1977 | 1981 | 199 | 400/220 | Oil | ODAF | Autotransformer (3 single-phase units) | Outdoor | C | 0 | - | 0 | 26.8 | Between 2 and 5
45 | 85 | 1977 | 1979 | 197.5 | 400/220 | Oil | ODAF | Autotransformer (3 single-phase units) | Outdoor | C | 0 | - | 0 | 26.6 | Between 2 and 5
45 | 124 | 1989 | 1991 | 47.8 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 24.085 | 0 | 19.1 | Between 2 and 5
45 | 124 | 1980 | 1981 | 50.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 25.145 | 0 | 20 | Between 2 and 5
45 | 124 | 2016 | 2016 | 47.6 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 24.73 | 0 | 19.6 | Between 2 and 5
46 | 125 | 2016 | 2016 | 40.9 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 29.89 | 0 | 17.6 | Between 2 and 5
46 | 125 | 1973 | 1973 | 49.5 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 36.165 | 0 | 30.2 | Between 2 and 5
46 | 125 | 1979 | 1980 | 50.8 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 37.12 | 0 | 31 | Between 2 and 5
47 | 127 | 1980 | 1982 | 57.8 | 220/63 | Oil | ONAF | Transformer (3 single-phase units) | Outdoor | C | 0 | 33.94 | 0 | 26.9 | Between 2 and 5
47 | 127 | 2015 | 2015 | 47.8 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 28.24 | 0 | 16.6 | Between 2 and 5
47 | 127 | 2000 | 2013 | 55.3 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 32.475 | 0 | 25.8 | Between 2 and 5
48 | 129 | 1983 | 1984 | 64.4 | 220/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 15 | 44.47 | 0 | 37.1 | Between 2 and 5
48 | 129 | 1981 | 1983 | 67 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 15 | 46.255 | 0 | 36.7 | Between 2 and 5
48 | 129 | 2008 | 2008 | 56.3 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 38.89 | 0 | 22.9 | Between 2 and 5
49 | 130 | 1985 | 1986 | 67.4 | 220/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 45 | 52.255 | 0 | 43.5 | Between 2 and 5
49 | 130 | 1983 | 1984 | 68.2 | 220/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 45 | 52.525 | 0 | 43.8 | Between 2 and 5
49 | 130 | 1985 | 1986 | 67 | 220/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 45 | 51.395 | 0 | 42.8 | Between 2 and 5
49 | 130 | 1993 | 1994 | 67.5 | 220/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 30 | 51.985 | 0 | 41.2 | Between 2 and 5
50 | 89 | 2011 | 2011 | 150 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 21.1 | Between 2 and 5
50 | 89 | 1991 | 1992 | 187.4 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 26.4 | Between 2 and 5
50 | 89 | 1984 | 1986 | 182.2 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 25.9 | Between 2 and 5
51 | 90 | 2010 | 2010 | 70.9 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 8.3 | Between 2 and 5
52 | 132 | 2001 | 2001 | 38.2 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 22.515 | 0 | 17.9 | Between 2 and 5
53 | 134 | 2010 | 2011 | 38.7 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 18.735 | 0 | 11 | Between 2 and 5
53 | 134 | 1995 | 1996 | 43.1 | 220/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 20.83 | 0 | 16.5 | Between 2 and 5
53 | 134 | 2007 | 2007 | 38.5 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 18.635 | 0 | 11 | Between 2 and 5
55 | 135 | 1994 | 1994 | 70.9 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 44.18 | 0 | 26 | Between 2 and 5
55 | 135 | 1979 | 1995 | 50.5 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 31.49 | 0 | 26.3 | Between 2 and 5
55 | 135 | 1982 | 1995 | 51.6 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 32.05 | 0 | 26.7 | Between 2 and 5
55 | 135 | 2011 | 2012 | 49.8 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 30.69 | 0 | 18.1 | Between 2 and 5
56 | 136 | 2002 | 2002 | 84.3 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 53.855 | 0 | 31.7 | Between 2 and 5
56 | 136 | 2003 | 2003 | 83.8 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 53.535 | 0 | 31.5 | Between 2 and 5
56 | 136 | 2003 | 2003 | 84.5 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 53.965 | 0 | 31.8 | Between 2 and 5
57 | 93 | 1991 | 1991 | 112.6 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 11.8 | Between 2 and 5
57 | 93 | 1989 | 1990 | 111.7 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 11.8 | Between 2 and 5
57 | 138 | 2000 | 2001 | 26.3 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 18.11 | 0 | 14.4 | Between 2 and 5
57 | 138 | 2009 | 2009 | 25.1 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 17.13 | 0 | 10.1 | Between 2 and 5
57 | 138 | 2017 | 2019 | 97.7 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 30 | 66.675 | 0 | 39.2 | Between 2 and 5
58 | 139 | 1998 | 1999 | 68.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 42.52 | 0 | 25 | Between 2 and 5
58 | 139 | 2004 | 2005 | 69.7 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 42.615 | 0 | 25.1 | Between 2 and 5
58 | 139 | 2006 | 2006 | 70.8 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 43.285 | 0 | 25.4 | Between 2 and 5
59 | 143 | 2015 | 2015 | 25.3 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 16.69 | 0 | 9.8 | Between 2 and 5
59 | 143 | 2015 | 2015 | 25.2 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 16.665 | 0 | 9.8 | Between 2 and 5
60 | 144 | 2008 | 2008 | 35.7 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 18.105 | 0 | 10.6 | Between 2 and 5
60 | 144 | 1993 | 1993 | 39.5 | 220/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 20.03 | 0 | 15.9 | Between 2 and 5
62 | 152 | 2010 | 2010 | 23.9 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 12.32 | 0 | 9.8 | Between 2 and 5
62 | 152 | 1992 | 2011 | 24 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 12.36 | 0 | 9.8 | Between 2 and 5
62 | 152 | 1983 | 2002 | 12.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 6.53 | 0 | 10.4 | Between 2 and 5
63 | 153 | 1994 | 1995 | 5.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 3.13 | 0 | 4.9 | Between 2 and 5
63 | 153 | 1992 | 1993 | 5.2 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 3.045 | 0 | 4.8 | Between 2 and 5
64 | 154 | 1990 | 2005 | 49.2 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 34.545 | 0 | 27.4 | Between 2 and 5
64 | 154 | 2006 | 2006 | 49.6 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 34.795 | 0 | 27.6 | Between 2 and 5
65 | 155 | 2009 | 2010 | 35.7 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 17.735 | 0 | 14.1 | Between 2 and 5
65 | 155 | 2015 | 2015 | 44.2 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 21.96 | 0 | 17.4 | Between 2 and 5
65 | 155 | 2016 | 2016 | 43.5 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 21.59 | 0 | 17.2 | Between 2 and 5
66 | 156 | 2006 | 2008 | 78.2 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 36.855 | 0 | 21.7 | Between 2 and 5
66 | 156 | 2012 | 2012 | 77.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 36.3 | 0 | 21.4 | Between 2 and 5
68 | 157 | 2011 | 2011 | 43.9 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 31.03 | 0 | 18.3 | Between 2 and 5
68 | 157 | 2011 | 2012 | 44.1 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 31.175 | 0 | 18.3 | Between 2 and 5
69 | 101 | 2007 | 2007 | 138.8 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 14.5 | Between 2 and 5
71 | 161 | 2006 | 2007 | 82.2 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 27.03 | 0 | 15.9 | Between 2 and 5
71 | 161 | 2010 | 2010 | 78.8 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 25.895 | 0 | 15.2 | Between 2 and 5
73 | 165 | 2005 | 2011 | 20.6 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 8.95 | 0 | 7.1 | Between 2 and 5
73 | 165 | 2007 | 2008 | 21.7 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 9.47 | 0 | 7.5 | Between 2 and 5
74 | 166 | 2010 | 2010 | 62.3 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 22.465 | 0 | 13.2 | Between 2 and 5
74 | 166 | 2008 | 2008 | 62 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 22.36 | 0 | 13.1 | Between 2 and 5
75 | 167 | 2015 | 2015 | 15.1 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 7.875 | 0 | 4.6 | Between 2 and 5
75 | 167 | 1969 | 2009 | 19.7 | 220/63 | Oil | ONAF | Transformer (3 single-phase units) | Outdoor | C | 0 | 9.505 | 0 | 7.9 | Between 2 and 5
75 | 167 | 1973 | 2008 | 19.1 | 220/63 | Oil | ONAF | Transformer (3 single-phase units) | Outdoor | C | 0 | 9.25 | 0 | 7.7 | Between 2 and 5
76 | 168 | 2010 | 2011 | 20.4 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 12.98 | 0 | 7.6 | Between 2 and 5
76 | 168 | 2010 | 2011 | 20.6 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 13.125 | 0 | 7.7 | Between 2 and 5
76 | 168 | 2017 | 2019 | 127.5 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 60 | 86.385 | 0 | 50.8 | Between 2 and 5
77 | 106 | 2011 | 2011 | 130.2 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 12.3 | Between 2 and 5
77 | 106 | 2009 | 2010 | 132 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 12.5 | Between 2 and 5
77 | 106 | 2010 | 2010 | 129.9 | 400/220 | Oil | ODAF | Autotransformer (1 three-phase unit) | Outdoor | C | 0 | - | 0 | 12.3 | Between 2 and 5
78 | 170 | 2016 | 2018 | 30.4 | 220/63 | Oil | ONAF | Transformer (3 single-phase units) | Outdoor | C | 0 | 10.49 | 0 | 8.3 | Between 2 and 5
78 | 170 | 2009 | 2009 | 31 | 220/63 | Oil | ONAF | Transformer (3 single-phase units) | Outdoor | C | 0 | 10.675 | 0 | 8.5 | Between 2 and 5
79 | 172 | 2007 | 2012 | 12.9 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 7.025 | 0 | 5.6 | Between 2 and 5
79 | 172 | 1990 | 2012 | 13.7 | 220/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 7.425 | 0 | 5.9 | Between 2 and 5
81 | 116 | 2012 | 2013 | 76.5 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Indoor | C | 0 | 64.33 | 0 | 37.8 | Between 2 and 5
81 | 116 | 2012 | 2013 | 76.6 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Indoor | C | 0 | 64.43 | 0 | 37.9 | Between 2 and 5
82 | 119 | 1995 | 2003 | 83.3 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 50.84 | 0 | 29.9 | Between 2 and 5
82 | 119 | 2002 | 2003 | 82.3 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 50.235 | 0 | 29.6 | Between 2 and 5
82 | 119 | 2009 | 2009 | 82.9 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 50.595 | 0 | 29.8 | Between 2 and 5
83 | 122 | 2005 | 2006 | 81.6 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 55.345 | 0 | 32.6 | Between 2 and 5
83 | 122 | 2008 | 2008 | 82.2 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 55.56 | 0 | 32.7 | Between 2 and 5
83 | 122 | 2010 | 2011 | 81.6 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 55.155 | 0 | 32.5 | Between 2 and 5
88 | 128 | 1988 | 1989 | 85.7 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 15 | 58.295 | 0 | 34.3 | Between 2 and 5
88 | 128 | 1993 | 1993 | 85.7 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 15 | 58.31 | 0 | 34.3 | Between 2 and 5
89 | 131 | 2011 | 2012 | 42.5 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 21.925 | 0 | 12.9 | Between 2 and 5
89 | 131 | 1995 | 1996 | 42.3 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 22.1 | 0 | 13 | Between 2 and 5
89 | 131 | 1992 | 1993 | 41.1 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 21.205 | 0 | 12.5 | Between 2 and 5
92 | 137 | 2011 | 2013 | 66.6 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 40.425 | 0 | 23.8 | Between 2 and 5
92 | 137 | 2013 | 2013 | 64.6 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 39.97 | 0 | 23.5 | Between 2 and 5
95 | 145 | 2018 | 2019 | 59.4 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 33.465 | 0 | 19.7 | Between 2 and 5
95 | 145 | 2008 | 2008 | 14.2 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 9.415 | 0 | 5.5 | Between 2 and 5
95 | 145 | 2001 | 2002 | 13.9 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 8.485 | 0 | 5 | Between 2 and 5
97 | 147 | 2016 | 2017 | 81.9 | 400/63 | Oil | ONAF | Transformer (1 three-phase unit) | Outdoor | A | 0 | 51.65 | 81 | 30.4 | Between 2 and 5
101 | 158 | 2006 | 2006 | 51.3 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 31.245 | 0 | 18.4 | Between 2 and 5
101 | 158 | 2011 | 2011 | 50.9 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 31.025 | 0 | 18.2 | Between 2 and 5
103 | 160 | 2009 | 2010 | 43.4 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 26.38 | 0 | 15.5 | Between 2 and 5
103 | 160 | 2009 | 2010 | 43.6 | 400/63 | Oil | ODAF | Transformer (1 three-phase unit) | Outdoor | C | 0 | 26.46 | 0 | 15.6 | Between 2 and 5
105 | 164 | 2007 | 2007 | 36.6 | 400/63 | Oil | ODAF | Transformer (3 single-phase units) | Outdoor | C | 0 | 18.275 | 0 | 10.8 | Between 2 and 5
105 | 164 | 2011 | 2011 | 36.1 | 400/63 | Oil | ODAF | Transformer (3 single-phase units) | Outdoor | C | 0 | 18.03 | 0 | 10.6 | Between 2 and 5

## Lines_Cables Data
fbus | tbus | Length (km) | Type of installation | Summer rating [MVA] | Spring rating [MVA] | Autumn rating [MVA] | Winter rating [MVA] | Conductor cross-sectional area [mm2] | Rated voltage [kV] | Conductor material | Criticallity indicator | Time over rating 50% [%] | Clients affected | ENS in fault [MWh] | Mean load [%] | Value of lost load [k€/MWh]
8 | 24 | 54 | overhead | 91 | 123 | 130 | 130 | Bear | 150 | Al | - | 0 | - | 0 | 0 | Between 2 and 5
8 | 176 | 36.6 | overhead | 96 | 104 | 104 | 104 | Bear | 150 | Al | C | 15 | - | 0 | 9.8 | Between 2 and 5
8 | 176 | 36.7 | overhead | 96 | 104 | 104 | 104 | Bear | 150 | Al | C | 15 | - | 0 | 9.8 | Between 2 and 5
9 | 14 | 4.3 | overhead | 255 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 12.3 | Between 2 and 5
9 | 14 | 4.2 | overhead | 255 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 12.6 | Between 2 and 5
9 | 14 | 4.1 | overhead | 124 | 162 | 183 | 203 | Zebra | 150 | Al | C | 0 | - | 0 | 20.8 | Between 2 and 5
10 | 19 | 61.3 | overhead | 218 | 248 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 17.4 | Between 2 and 5
10 | 22 | 44.5 | overhead | 164 | 186 | 196 | 206 | Bear | 150 | Al | C | 0 | - | 0 | 10.6 | Between 2 and 5
10 | 26 | 26 | overhead | 260 | 260 | 260 | 260 | 570 | 150 | Al | C | 0 | - | 0 | 9.2 | Between 2 and 5
11 | 14 | 36.7 | overhead | 171 | 186 | 196 | 206 | Bear | 150 | Al | C | 0 | - | 0 | 11 | Between 2 and 5
11 | 14 | 36.5 | overhead | 191 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 10.3 | Between 2 and 5
12 | 22 | 61.6 | overhead | 189 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 13.1 | Between 2 and 5
12 | 23 | 49.8 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 5.5 | Between 2 and 5
12 | 29 | 27.9 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 14.5 | Between 2 and 5
12 | 29 | 27.9 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 14.5 | Between 2 and 5
12 | 29 | 42.8 | overhead | 260 | 260 | 260 | 260 | Zambeze | 150 | Al | C | 0 | - | 0 | 10.6 | Between 2 and 5
12 | 34 | 68.7 | overhead | 255 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 5.2 | Between 2 and 5
13 | 14 | 23.1 | overhead | 255 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 6.4 | Between 2 and 5
13 | 14 | 23.1 | overhead | 255 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 6.4 | Between 2 and 5
13 | 20 | 13.6 | overhead | 195 | 204 | 214 | 221 | Bear | 150 | Al | C | 0 | - | 0 | 16.2 | Between 2 and 5
13 | 20 | 13.6 | overhead | 195 | 204 | 214 | 221 | Bear | 150 | Al | C | 0 | - | 0 | 16.2 | Between 2 and 5
13 | 180 | 12 | overhead | 255 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 5.4 | Between 2 and 5
13 | 246 | 12.2 | overhead | 260 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 3.5 | Between 2 and 5
14 | 180 | 12 | overhead | 255 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 6.9 | Between 2 and 5
14 | 185 | 20.5 | overhead | 191 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 14.9 | Between 2 and 5
14 | 186 | 48.4 | overhead | 185 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 9.2 | Between 2 and 5
14 | 246 | 12 | overhead | 255 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 9.4 | Between 2 and 5
15 | 22 | 63.4 | overhead | 224 | 248 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 14.5 | Between 2 and 5
15 | 22 | 63.4 | overhead | 224 | 248 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 14.5 | Between 2 and 5
15 | 26 | 32.6 | overhead | 260 | 260 | 260 | 260 | 570 | 150 | Al | C | 0 | - | 0 | 9.8 | Between 2 and 5
15 | 27 | 50.5 | overhead | 191 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 15.1 | Between 2 and 5
15 | 28 | 60.7 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 14.3 | Between 2 and 5
15 | 29 | 95.6 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 14.2 | Between 2 and 5
15 | 183 | 12.8 | overhead | 340 | 340 | 340 | 340 | Zambeze | 150 | Al | B | 60 | - | 0 | 53.6 | Between 2 and 5
15 | 250 | 5.4 | overhead | 130 | 130 | 130 | 130 | Zebra | 150 | Al | C | 0 | - | 0 | 10.3 | Between 2 and 5
15 | 250 | 5.5 | overhead | 130 | 130 | 130 | 130 | Zebra | 150 | Al | C | 0 | - | 0 | 10.1 | Between 2 and 5
15 | 255 | 5.9 | overhead | 260 | 273 | 285 | 296 | Zebra | 150 | Al | A | 0 | 1 | 33.7 | 11.7 | Between 2 and 5
16 | 178 | 19 | overhead | 104 | 123 | 130 | 130 | Bear | 150 | Al | C | 0 | - | 0 | 6.8 | Between 2 and 5
17 | 21 | 37.9 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 9.8 | Between 2 and 5
17 | 21 | 35 | overhead | 260 | 273 | 285 | 296 | Zebra | 150 | Al | C | 0 | - | 0 | 8.8 | Between 2 and 5
17 | 25 | 35.2 | overhead | 104 | 123 | 139 | 153 | Bear | 150 | Al | C | 0 | - | 0 | 21.5 | Between 2 and 5
17 | 184 | 16.6 | overhead | 91 | 108 | 121 | 134 | Panther | 150 | Al | C | 55 | - | 0 | 61.9 | Between 2 and 5
18 | 25 | 23.6 | overhead | 104 | 123 | 139 | 153 | Bear | 150 | Al | C | 0 | - | 0 | 12.7 | Between 2 and 5
18 | 25 | 23.6 | overhead | 104 | 123 | 139 | 153 | Bear | 150 | Al | C | 0 | - | 0 | 12.7 | Between 2 and 5
18 | 32 | 41.7 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 11.1 | Between 2 and 5
19 | 186 | 48.4 | overhead | 185 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 9.2 | Between 2 and 5
21 | 30 | 33.3 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 20.7 | Between 2 and 5
21 | 251 | 26.5 | overhead | 260 | 273 | 285 | 296 | Zebra | 150 | Al | C | 0 | - | 0 | 11.2 | Between 2 and 5
22 | 34 | 57.9 | overhead | 337 | 372 | 392 | 411 | Bear | 150 | Al | C | 0 | - | 0 | 8.4 | Between 2 and 5
22 | 245 | 22 | overhead | 81 | 123 | 130 | 130 | Bear | 150 | Al | A | 0 | 1 | 36.2 | 31.4 | Between 2 and 5
23 | 34 | 35.1 | overhead | 255 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 13.8 | Between 2 and 5
23 | 34 | 35.1 | overhead | 255 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 13.8 | Between 2 and 5
23 | 34 | 42.7 | overhead | 255 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 11.3 | Between 2 and 5
24 | 31 | 46.5 | overhead | 520 | 520 | 520 | 520 | Zambeze | 150 | Al | C | 0 | - | 0 | 9.6 | Between 2 and 5
24 | 35 | 88.8 | overhead | 253 | 273 | 285 | 296 | Zebra | 150 | Al | A | 0 | - | 66.3 | 15.5 | Between 2 and 5
24 | 181 | 7.8 | overhead | 189 | 195 | 195 | 195 | Bear | 150 | Al | C | 15 | - | 0 | 12.7 | Between 2 and 5
24 | 248 | 20.8 | overhead | 227 | 248 | 381 | 381 | Zebra | 150 | Al | C | 0 | - | 0 | 7.7 | Between 2 and 5
24 | 248 | 20.8 | overhead | 227 | 248 | 381 | 381 | Zebra | 150 | Al | C | 0 | - | 0 | 7.7 | Between 2 and 5
24 | 252 | 36.3 | overhead | 253 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 12.5 | Between 2 and 5
25 | 32 | 19.3 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 22.5 | Between 2 and 5
25 | 32 | 19.3 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 22.5 | Between 2 and 5
25 | 32 | 18 | overhead | 233 | 248 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 25.1 | Between 2 and 5
27 | 185 | 20.5 | overhead | 191 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 14.9 | Between 2 and 5
28 | 29 | 35.2 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 14 | Between 2 and 5
30 | 32 | 13.2 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 12.3 | Between 2 and 5
30 | 32 | 13.2 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 12.3 | Between 2 and 5
30 | 32 | 15.4 | overhead | 195 | 204 | 214 | 222 | Bear | 150 | Al | C | 0 | - | 0 | 10.5 | Between 2 and 5
30 | 33 | 19.8 | overhead | 520 | 520 | 520 | 520 | Zambeze | 150 | Al | C | 0 | - | 0 | 9.5 | Between 2 and 5
30 | 174 | 13.8 | overhead | 260 | 260 | 260 | 260 | Zambeze | 150 | Al | C | 0 | - | 0 | 12.4 | Between 2 and 5
30 | 179 | 7.3 | overhead | 104 | 123 | 139 | 153 | Bear | 150 | Al | C | 15 | - | 0 | 10.3 | Between 2 and 5
30 | 184 | 16.6 | overhead | 91 | 108 | 121 | 134 | Panther | 150 | Al | C | 0 | - | 0 | 14 | Between 2 and 5
31 | 248 | 20.8 | overhead | 227 | 248 | 381 | 381 | Zebra | 150 | Al | C | 0 | - | 0 | 7.8 | Between 2 and 5
31 | 248 | 20.8 | overhead | 227 | 248 | 381 | 381 | Zebra | 150 | Al | C | 0 | - | 0 | 7.8 | Between 2 and 5
31 | 253 | 31.9 | overhead | 253 | 260 | 260 | 260 | Zebra | 150 | Al | C | 0 | - | 0 | 8.7 | Between 2 and 5
32 | 33 | 32.2 | overhead | 504 | 520 | 520 | 520 | Rail | 150 | Al | C | 0 | - | 0 | 7.8 | Between 2 and 5
32 | 254 | 53.5 | overhead | 260 | 273 | 285 | 296 | Zebra | 150 | Al | C | 0 | - | 0 | 17.6 | Between 2 and 5
32 | 254 | 53.5 | overhead | 260 | 273 | 285 | 296 | Zebra | 150 | Al | C | 0 | - | 0 | 17.6 | Between 2 and 5
33 | 173 | 3 | overhead | 306 | 321 | 335 | 348 | Zambeze | 150 | Al | C | 0 | - | 0 | 7.7 | Between 2 and 5
33 | 177 | 15.3 | overhead | 104 | 104 | 104 | 104 | Bear | 150 | Al | C | 15 | - | 0 | 8.3 | Between 2 and 5
33 | 182 | 0.9 | overhead | 306 | 321 | 335 | 348 | Zambeze | 150 | Al | C | 45 | - | 0 | 29.5 | Between 2 and 5
33 | 184 | 19.3 | overhead | 274 | 291 | 307 | 322 | Zambeze | 150 | Al | C | 0 | - | 0 | 18.2 | Between 2 and 5
36 | 64 | 52.3 | overhead | 666 | 728 | 766 | 804 | Zebra | 220 | Al | C | 0 | - | 0 | 17.3 | Between 2 and 5
36 | 71 | 48.9 | overhead | 666 | 728 | 766 | 804 | Zebra | 220 | Al | C | 0 | - | 0 | 24 | Between 2 and 5
36 | 187 | 0.7 | overhead | 191 | 191 | 191 | 191 | Zebra | 220 | Al | C | 0 | - | 0 | 2.4 | Between 2 and 5
36 | 188 | 0.7 | overhead | 191 | 191 | 191 | 191 | Zebra | 220 | Al | C | 0 | - | 0 | 5.7 | Between 2 and 5
36 | 189 | 0.8 | overhead | 191 | 191 | 191 | 191 | Zebra | 220 | Al | C | 0 | - | 0 | 5.8 | Between 2 and 5
37 | 59 | 10.4 | underground | 493 | 493 | 493 | 493 | 1600 | 220 | Cu | C | 0 | - | 0 | 11.9 | Between 2 and 5
37 | 213 | 1.8 | underground | 322 | 322 | 322 | 322 | 1000 | 220 | Al | C | 0 | - | 0 | 9.1 | Between 2 and 5
37 | 214 | 1.8 | underground | 322 | 322 | 322 | 322 | 1000 | 220 | Al | C | 0 | - | 0 | 20.5 | Between 2 and 5
37 | 215 | 1.8 | underground | 322 | 322 | 322 | 322 | 1000 | 220 | Al | C | 0 | - | 0 | 5.7 | Between 2 and 5
37 | 216 | 1.8 | underground | 322 | 322 | 322 | 322 | 1000 | 220 | Al | C | 0 | - | 0 | 20.8 | Between 2 and 5
38 | 208 | 3.2 | underground | 493 | 493 | 493 | 493 | 1600 | 220 | Cu | C | 0 | - | 0 | 12.9 | Between 2 and 5
38 | 209 | 3.2 | underground | 493 | 493 | 493 | 493 | 1600 | 220 | Cu | C | 0 | - | 0 | 15.2 | Between 2 and 5
39 | 45 | 106.8 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 19.9 | Between 2 and 5
39 | 69 | 43 | overhead | 342 | 364 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 17.9 | Between 2 and 5
39 | 69 | 43 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 17.5 | Between 2 and 5
39 | 71 | 22.2 | overhead | 684 | 727 | 762 | 762 | Zebra | 220 | Al | C | 0 | - | 0 | 9.6 | Between 2 and 5
39 | 78 | 41.1 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 10.7 | Between 2 and 5
39 | 195 | 30.4 | overhead | 199 | 237 | 269 | 297 | Zebra | 220 | Al | C | 0 | - | 0 | 15.7 | Between 2 and 5
39 | 199 | 54.7 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 18 | Between 2 and 5
39 | 258 | 20.3 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 7.6 | Between 2 and 5
39 | 258 | 15.1 | overhead | 199 | 237 | 269 | 297 | Zebra | 220 | Al | C | 0 | - | 0 | 17 | Between 2 and 5
40 | 51 | 54.7 | overhead | 374 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 12.9 | Between 2 and 5
40 | 65 | 61.9 | overhead | 333 | 364 | 381 | 381 | Zebra | 220 | Al | C | 15 | - | 0 | 16.9 | Between 2 and 5
40 | 65 | 61.8 | overhead | 333 | 364 | 381 | 381 | Zebra | 220 | Al | C | 15 | - | 0 | 17.2 | Between 2 and 5
40 | 196 | 1 | overhead | 182 | 237 | 269 | 297 | Zebra | 220 | Al | C | 0 | - | 0 | 9.7 | Between 2 and 5
40 | 198 | 19.6 | overhead | 439 | 471 | 491 | 511 | Zambeze | 220 | Al | C | 0 | - | 0 | 11.5 | Between 2 and 5
40 | 5 | 41.1 | overhead | 374 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 9.5 | Between 2 and 5
40 | 5 | 41.4 | overhead | 374 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 9.4 | Between 2 and 5
40 | 6 | 30.2 | overhead | 360 | 390 | 418 | 430 | Zebra | 220 | Al | C | 0 | - | 0 | 15.1 | Between 2 and 5
41 | 53 | 10.4 | overhead | 381 | 381 | 381 | 381 | Zambeze | 220 | Al | C | 0 | - | 0 | 4.9 | Between 2 and 5
41 | 53 | 6.5 | overhead | 381 | 381 | 381 | 381 | Zambeze | 220 | Al | C | 0 | - | 0 | 7.5 | Between 2 and 5
41 | 57 | 20.2 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 15.6 | Between 2 and 5
41 | 68 | 7 | overhead | 401 | 426 | 450 | 472 | Zambeze | 220 | Al | C | 0 | - | 0 | 6.1 | Between 2 and 5
41 | 68 | 10.7 | underground | 493 | 493 | 493 | 493 | 1600 | 220 | Cu | C | 0 | - | 0 | 9.2 | Between 2 and 5
41 | 210 | 9.4 | overhead | 762 | 762 | 762 | 762 | Zambeze | 220 | Al | C | 0 | - | 0 | 9 | Between 2 and 5
41 | 211 | 37 | overhead | 762 | 762 | 762 | 762 | Zambeze | 220 | Al | C | 0 | - | 0 | 3.1 | Between 2 and 5
42 | 78 | 28 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 11.5 | Between 2 and 5
42 | 78 | 28 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 11.5 | Between 2 and 5
42 | 257 | 17.3 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 17.5 | Between 2 and 5
42 | 257 | 17.3 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 17.7 | Between 2 and 5
43 | 58 | 12.6 | underground | 493 | 493 | 493 | 493 | 1600 | 220 | Cu | C | 0 | - | 0 | 11.7 | Between 2 and 5
43 | 76 | 11.1 | underground | 446 | 446 | 446 | 446 | 1600 | 220 | Cu | C | 0 | - | 0 | 14.2 | Between 2 and 5
43 | 76 | 11.1 | underground | 446 | 446 | 446 | 446 | 1600 | 220 | Cu | C | 0 | - | 0 | 14.2 | Between 2 and 5
43 | 204 | 9.2 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 2.3 | Between 2 and 5
43 | 205 | 3.9 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 12.1 | Between 2 and 5
43 | 219 | 5.4 | overhead | 342 | 364 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 10.6 | Between 2 and 5
44 | 48 | 24.9 | overhead | 342 | 364 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 20.7 | Between 2 and 5
44 | 66 | 50.9 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 14 | Between 2 and 5
44 | 66 | 50.7 | overhead | 897 | 941 | 982 | 1021 | Zambeze | 220 | Al | C | 0 | - | 0 | 7.4 | Between 2 and 5
44 | 193 | 31.7 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 21.4 | Between 2 and 5
45 | 46 | 40.2 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 14.2 | Between 2 and 5
45 | 46 | 38.8 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 15.8 | Between 2 and 5
45 | 46 | 38.8 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 15.7 | Between 2 and 5
45 | 74 | 36.7 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 21.7 | Between 2 and 5
45 | 199 | 54.7 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 19.5 | Between 2 and 5
46 | 50 | 25.4 | overhead | 381 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 18.9 | Between 2 and 5
46 | 64 | 34.8 | overhead | 666 | 728 | 766 | 804 | Zebra | 220 | Al | C | 0 | - | 0 | 14.9 | Between 2 and 5
46 | 214 | 30 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 17.9 | Between 2 and 5
46 | 216 | 28.9 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 16.8 | Between 2 and 5
46 | 222 | 0.8 | overhead | 438 | 438 | 438 | 438 | Zebra | 220 | Al | B | 55 | - | 0 | 44.6 | Between 2 and 5
46 | 260 | 56.8 | overhead | 342 | 364 | 381 | 381 | Zebra | 220 | Al | A | 0 | 1 | 109.6 | 27 | Between 2 and 5
47 | 57 | 65 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 9.9 | Between 2 and 5
47 | 61 | 2.1 | overhead | 199 | 237 | 269 | 297 | Zebra | 220 | Al | C | 0 | - | 0 | 10.5 | Between 2 and 5
47 | 66 | 33.4 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 13.4 | Between 2 and 5
47 | 67 | 50 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 9.7 | Between 2 and 5
47 | 75 | 45 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 13.2 | Between 2 and 5
47 | 197 | 42.1 | overhead | 762 | 762 | 762 | 762 | Rail | 220 | Al | - | 0 | - | 0 | 0 | Between 2 and 5
47 | 211 | 37 | overhead | 762 | 762 | 762 | 762 | Zambeze | 220 | Al | C | 0 | - | 0 | 12.3 | Between 2 and 5
47 | 224 | 6.4 | overhead | 750 | 762 | 762 | 762 | Zambeze | 220 | Al | C | 0 | - | 0 | 9.7 | Between 2 and 5
48 | 66 | 69.5 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 15.2 | Between 2 and 5
48 | 69 | 22.6 | overhead | 342 | 364 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 14.4 | Between 2 and 5
48 | 69 | 22 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 13.6 | Between 2 and 5
49 | 57 | 21.4 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 9.9 | Between 2 and 5
49 | 193 | 9.2 | overhead | 1200 | 1200 | 1200 | 1200 | Zambeze | 220 | Al | C | 0 | - | 0 | 5.5 | Between 2 and 5
49 | 221 | 13.7 | overhead | 762 | 762 | 762 | 762 | Zambeze | 220 | Al | C | 0 | - | 0 | 16.1 | Between 2 and 5
50 | 55 | 19.5 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 13 | Between 2 and 5
50 | 55 | 15.8 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 15.6 | Between 2 and 5
50 | 56 | 27 | overhead | 762 | 762 | 762 | 762 | Zambeze | 220 | Al | C | 0 | - | 0 | 11.2 | Between 2 and 5
50 | 204 | 9.2 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 22 | Between 2 and 5
50 | 213 | 13.3 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 7.9 | Between 2 and 5
50 | 215 | 19.7 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 4.9 | Between 2 and 5
50 | 217 | 11.3 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 8.8 | Between 2 and 5
51 | 66 | 45.9 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 9.1 | Between 2 and 5
51 | 66 | 46 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 9.1 | Between 2 and 5
51 | 194 | 29.4 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 9.2 | Between 2 and 5
51 | 194 | 29.5 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 9.1 | Between 2 and 5
51 | 197 | 2.2 | overhead | 825 | 864 | 902 | 938 | Rail | 220 | Al | C | 0 | - | 0 | 7.9 | Between 2 and 5
51 | 224 | 6.4 | overhead | 750 | 762 | 762 | 762 | Zambeze | 220 | Al | - | 0 | - | 0 | 0 | Between 2 and 5
52 | 199 | 3.6 | overhead | 191 | 191 | 191 | 191 | Zebra | 220 | Al | C | 0 | - | 0 | 11.5 | Between 2 and 5
53 | 68 | 6.6 | overhead | 401 | 426 | 450 | 472 | Zambeze | 220 | Al | C | 0 | - | 0 | 1.4 | Between 2 and 5
53 | 190 | 14.7 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 7.8 | Between 2 and 5
54 | 63 | 25.7 | overhead | 374 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 13.1 | Between 2 and 5
54 | 77 | 39.5 | overhead | 374 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 12.1 | Between 2 and 5
54 | 77 | 46.1 | overhead | 374 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 11 | Between 2 and 5
54 | 191 | 14.9 | overhead | 182 | 229 | 229 | 229 | Zebra | 220 | Al | C | 0 | - | 0 | 19.7 | Between 2 and 5
54 | 191 | 15.5 | overhead | 229 | 229 | 229 | 229 | Zambeze | 220 | Al | C | 0 | - | 0 | 19 | Between 2 and 5
54 | 192 | 19.4 | overhead | 374 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 11.4 | Between 2 and 5
54 | 200 | 0.4 | overhead | 182 | 237 | 269 | 297 | Zebra | 220 | Al | C | 0 | - | 0 | 0.2 | Between 2 and 5
54 | 201 | 0.4 | overhead | 182 | 237 | 269 | 297 | Zebra | 220 | Al | C | 0 | - | 0 | 6.8 | Between 2 and 5
54 | 202 | 0.4 | overhead | 182 | 237 | 269 | 297 | Zebra | 220 | Al | C | 0 | - | 0 | 9.6 | Between 2 and 5
54 | 203 | 0.2 | overhead | 182 | 237 | 269 | 297 | Zebra | 220 | Al | C | 15 | - | 0 | 21.9 | Between 2 and 5
55 | 58 | 7.8 | underground | 364 | 364 | 364 | 364 | 1240 | 220 | Cu | C | 0 | - | 0 | 15.5 | Between 2 and 5
55 | 204 | 2.6 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 20.3 | Between 2 and 5
55 | 205 | 3.9 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 4.2 | Between 2 and 5
56 | 74 | 46 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 13.1 | Between 2 and 5
56 | 205 | 8.9 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 13.5 | Between 2 and 5
57 | 60 | 20.8 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 10.8 | Between 2 and 5
57 | 67 | 15.7 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 9.6 | Between 2 and 5
57 | 190 | 14.7 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 22.8 | Between 2 and 5
57 | 210 | 9.4 | overhead | 762 | 762 | 762 | 762 | Zambeze | 220 | Al | C | 0 | - | 0 | 13.8 | Between 2 and 5
57 | 220 | 10.4 | overhead | 1200 | 1200 | 1200 | 1200 | Zambeze | 220 | Al | C | 0 | - | 0 | 13.4 | Between 2 and 5
57 | 221 | 13.7 | overhead | 762 | 762 | 762 | 762 | Zambeze | 220 | Al | C | 0 | - | 0 | 14.7 | Between 2 and 5
58 | 219 | 6.2 | underground | 364 | 364 | 364 | 364 | 1200 | 220 | Cu | C | 0 | - | 0 | 10.7 | Between 2 and 5
59 | 217 | 12.5 | underground | 493 | 493 | 493 | 493 | 1600 | 220 | Cu | C | 0 | - | 0 | 7 | Between 2 and 5
60 | 66 | 12.8 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 7.4 | Between 2 and 5
60 | 206 | 0.2 | overhead | 191 | 191 | 191 | 191 | Zebra | 220 | Al | C | 0 | - | 0 | 7.1 | Between 2 and 5
60 | 207 | 0.3 | overhead | 191 | 191 | 191 | 191 | Zebra | 220 | Al | C | 0 | - | 0 | 11 | Between 2 and 5
62 | 212 | 12.5 | overhead | 374 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 17.5 | Between 2 and 5
62 | 259 | 36.5 | overhead | 376 | 381 | 381 | 381 | 570 | 220 | Al | C | 0 | - | 0 | 8.7 | Between 2 and 5
62 | 259 | 36.5 | overhead | 376 | 381 | 381 | 381 | 570 | 220 | Al | C | 0 | - | 0 | 8.7 | Between 2 and 5
62 | 261 | 27.5 | overhead | 370 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 10.3 | Between 2 and 5
62 | 261 | 27.5 | overhead | 370 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 10.3 | Between 2 and 5
63 | 194 | 74.1 | overhead | 374 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 11.3 | Between 2 and 5
65 | 257 | 17.3 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 17.6 | Between 2 and 5
65 | 257 | 17.3 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 17.8 | Between 2 and 5
65 | 259 | 36.5 | overhead | 376 | 381 | 381 | 381 | 570 | 220 | Al | C | 0 | - | 0 | 8.2 | Between 2 and 5
65 | 259 | 36.5 | overhead | 376 | 381 | 381 | 381 | 570 | 220 | Al | C | 0 | - | 0 | 8.2 | Between 2 and 5
66 | 218 | 0.3 | overhead | 381 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 12.3 | Between 2 and 5
69 | 70 | 42.1 | overhead | 762 | 762 | 762 | 762 | Rail | 220 | Al | C | 0 | - | 0 | 9.3 | Between 2 and 5
70 | 197 | 42.1 | overhead | 762 | 762 | 762 | 762 | Rail | 220 | Al | C | 0 | - | 0 | 9.3 | Between 2 and 5
71 | 78 | 66.3 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 9.4 | Between 2 and 5
71 | 78 | 66.3 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 9.4 | Between 2 and 5
72 | 261 | 27.5 | overhead | 370 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 10.7 | Between 2 and 5
72 | 261 | 27.5 | overhead | 370 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 10.7 | Between 2 and 5
73 | 77 | 45.6 | overhead | 374 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 12.6 | Between 2 and 5
73 | 79 | 52.6 | overhead | 762 | 762 | 762 | 762 | Zambeze | 220 | Al | C | 0 | - | 0 | 4.5 | Between 2 and 5
75 | 79 | 34.2 | overhead | 762 | 762 | 762 | 762 | Zambeze | 220 | Al | C | 0 | - | 0 | 3.2 | Between 2 and 5
75 | 267 | 0.4 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 9.8 | Between 2 and 5
77 | 192 | 26.1 | overhead | 374 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 9.9 | Between 2 and 5
77 | 192 | 26.2 | overhead | 374 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 10 | Between 2 and 5
78 | 223 | 13.2 | overhead | 342 | 364 | 383 | 402 | Zebra | 220 | Al | C | 10 | - | 0 | 21.5 | Between 2 and 5
78 | 258 | 20.3 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 13.9 | Between 2 and 5
80 | 87 | 59.4 | overhead | 1361 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 7.3 | Between 2 and 5
80 | 105 | 64.1 | overhead | 1361 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | A | 0 | - | 31.3 | 7.7 | Between 2 and 5
81 | 93 | 18.9 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 10.2 | Between 2 and 5
81 | 94 | 37 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 3 | Between 2 and 5
82 | 85 | 69.3 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 22.4 | Between 2 and 5
82 | 89 | 18.3 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 11 | Between 2 and 5
82 | 100 | 40.2 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 11.6 | Between 2 and 5
83 | 95 | 52.5 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 15.7 | Between 2 and 5
83 | 99 | 65.9 | overhead | 1386 | 1386 | 1386 | 1386 | Rail | 400 | Al | C | 0 | - | 0 | 15.1 | Between 2 and 5
83 | 100 | 80.9 | overhead | 1363 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 24.1 | Between 2 and 5
83 | 101 | 101.5 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 16.2 | Between 2 and 5
84 | 86 | 28.9 | overhead | 1321 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 6.4 | Between 2 and 5
84 | 100 | 83.9 | overhead | 1321 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 10.9 | Between 2 and 5
85 | 95 | 86.3 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 18.8 | Between 2 and 5
85 | 99 | 81.2 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 21.1 | Between 2 and 5
86 | 87 | 96 | overhead | 1321 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 13.8 | Between 2 and 5
86 | 97 | 15.9 | overhead | 1321 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 9.9 | Between 2 and 5
86 | 226 | 48.1 | overhead | 1321 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 8.3 | Between 2 and 5
87 | 102 | 97.8 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 14.7 | Between 2 and 5
87 | 226 | 48.1 | overhead | 1321 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 18.9 | Between 2 and 5
87 | 234 | 12.2 | overhead | 340 | 340 | 340 | 340 | Zambeze | 400 | Al | B | 50 | - | 0 | 53 | Between 2 and 5
87 | 235 | 12 | overhead | 340 | 340 | 340 | 340 | Zambeze | 400 | Al | B | 50 | - | 0 | 53 | Between 2 and 5
87 | 236 | 12 | overhead | 340 | 340 | 340 | 340 | Zambeze | 400 | Al | B | 50 | - | 0 | 53 | Between 2 and 5
88 | 93 | 29.4 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 23.8 | Between 2 and 5
88 | 93 | 34.1 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 20.3 | Between 2 and 5
88 | 96 | 59.6 | overhead | 1631 | 1711 | 1786 | 1856 | Zambeze | 400 | Al | C | 0 | - | 0 | 15.3 | Between 2 and 5
88 | 104 | 21.2 | overhead | 1631 | 1711 | 1786 | 1857 | Zambeze | 400 | Al | C | 0 | - | 0 | 20.5 | Between 2 and 5
89 | 97 | 53.6 | overhead | 1321 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 11 | Between 2 and 5
89 | 100 | 24.6 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 20.7 | Between 2 and 5
89 | 226 | 94.6 | overhead | 1386 | 1386 | 1386 | 1386 | 570 | 400 | Al | C | 0 | - | 0 | 10.7 | Between 2 and 5
90 | 93 | 74.8 | overhead | 1386 | 1386 | 1386 | 1386 | Rail | 400 | Al | C | 0 | - | 0 | 6.5 | Between 2 and 5
90 | 103 | 61.9 | overhead | 1386 | 1386 | 1386 | 1386 | Rail | 400 | Al | C | 0 | - | 0 | 11.4 | Between 2 and 5
90 | 106 | 87.6 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 10.3 | Between 2 and 5
90 | 231 | 39.8 | overhead | 1631 | 1711 | 1786 | 1857 | Zambeze | 400 | Al | C | 0 | - | 0 | 4.2 | Between 2 and 5
90 | 268 | 15.4 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 3.9 | Between 2 and 5
91 | 104 | 33 | overhead | 1386 | 1386 | 1386 | 1386 | Zebra | 400 | Al | C | 0 | - | 0 | 12.2 | Between 2 and 5
91 | 104 | 33.5 | overhead | 1386 | 1386 | 1386 | 1386 | Zebra | 400 | Al | C | 0 | - | 0 | 11.2 | Between 2 and 5
91 | 229 | 3.2 | overhead | 1631 | 1711 | 1786 | 1857 | Zambeze | 400 | Al | C | 0 | - | 0 | 4.2 | Between 2 and 5
91 | 229 | 3.1 | overhead | 1631 | 1711 | 1786 | 1857 | Zambeze | 400 | Al | C | 0 | - | 0 | 7.9 | Between 2 and 5
91 | 230 | 6.6 | overhead | 1631 | 1711 | 1786 | 1857 | Zambeze | 400 | Al | C | 0 | - | 0 | 5.8 | Between 2 and 5
92 | 93 | 23.3 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 20.5 | Between 2 and 5
92 | 95 | 111.8 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 17.5 | Between 2 and 5
93 | 94 | 46.4 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 2.9 | Between 2 and 5
93 | 101 | 85.3 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 17.9 | Between 2 and 5
95 | 101 | 63.7 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 13.6 | Between 2 and 5
95 | 241 | 12.7 | overhead | 528 | 528 | 528 | 528 | Zambeze | 400 | Al | B | 45 | - | 0 | 47.8 | Between 2 and 5
95 | 242 | 9.9 | overhead | 528 | 528 | 528 | 528 | Zambeze | 400 | Al | B | 30 | - | 0 | 25.9 | Between 2 and 5
96 | 104 | 39.1 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 21.2 | Between 2 and 5
96 | 232 | 0.4 | overhead | 350 | 350 | 350 | 350 | 1144 | 400 | Al | C | 15 | - | 0 | 20.3 | Between 2 and 5
96 | 233 | 0.4 | overhead | 350 | 350 | 350 | 350 | 1144 | 400 | Al | C | 45 | - | 0 | 30.6 | Between 2 and 5
96 | 1 | 1.1 | overhead | 1390 | 1400 | 1500 | 1660 | Rail | 400 | Al | C | 0 | - | 0 | 15.1 | Between 2 and 5
96 | 1 | 1.1 | overhead | 1390 | 1400 | 1500 | 1660 | Rail | 400 | Al | C | 0 | - | 0 | 15.1 | Between 2 and 5
98 | 99 | 40.9 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 12.4 | Between 2 and 5
98 | 3 | 25.7 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 10.5 | Between 2 and 5
99 | 237 | 0.2 | overhead | 340 | 340 | 340 | 340 | Zambeze | 400 | Al | B | 40 | - | 0 | 36.1 | Between 2 and 5
99 | 238 | 0.2 | overhead | 340 | 340 | 340 | 340 | Zambeze | 400 | Al | B | 40 | - | 0 | 36.1 | Between 2 and 5
99 | 243 | 0.2 | overhead | 505 | 505 | 505 | 505 | Zambeze | 400 | Al | C | 30 | - | 0 | 26.4 | Between 2 and 5
99 | 244 | 0.2 | overhead | 505 | 505 | 505 | 505 | Zambeze | 400 | Al | C | 30 | - | 0 | 19.8 | Between 2 and 5
100 | 239 | 0.3 | overhead | 438 | 438 | 438 | 438 | Zambeze | 400 | Al | B | 50 | - | 0 | 45.3 | Between 2 and 5
100 | 240 | 0.2 | overhead | 438 | 438 | 438 | 438 | Zambeze | 400 | Al | C | 25 | - | 0 | 34.1 | Between 2 and 5
101 | 103 | 60.6 | overhead | 1386 | 1386 | 1386 | 1386 | Rail | 400 | Al | C | 0 | - | 0 | 12.6 | Between 2 and 5
102 | 107 | 81.3 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 9.3 | Between 2 and 5
105 | 227 | 1.2 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 12.9 | Between 2 and 5
105 | 228 | 0.8 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 9 | Between 2 and 5
105 | 4 | 39.9 | overhead | 1280 | 1386 | 1386 | 1386 | Rail | 400 | Al | C | 0 | - | 0 | 14.8 | Between 2 and 5
106 | 225 | 29.4 | overhead | 1386 | 1386 | 1386 | 1386 | Zambeze | 400 | Al | C | 0 | - | 0 | 3.7 | Between 2 and 5
106 | 2 | 4.7 | overhead | 1469 | 1571 | 1641 | 1706 | Rail | 400 | Al | C | 0 | - | 0 | 13.9 | Between 2 and 5
107 | 7 | 33.9 | overhead | 1386 | 1386 | 1386 | 1386 | Rail | 400 | Al | C | 0 | - | 0 | 8.6 | Between 2 and 5
115 | 269 | 27.1 | overhead | 68.4 | 95.7 | 95.7 | 95.7 | 235 | 63 | Al | C | 0 | - | 0 | 6.6 | Between 2 and 5
116 | 279 | 0.7 | overhead | 141.9 | 148.1 | 148.1 | 148.1 | 380 | 63 | Al | C | 0 | - | 0 | 7.9 | Between 2 and 5
130 | 280 | 5.6 | overhead | 79.9 | 113.2 | 113.2 | 113.2 | 325 | 63 | Al | C | 0 | - | 0 | 10.3 | Between 2 and 5
130 | 280 | 4.9 | overhead | 79.9 | 113.2 | 113.2 | 113.2 | 325 | 63 | Al | C | 0 | - | 0 | 11.7 | Between 2 and 5
132 | 283 | 0.04 | overhead | 98.2 | 105.2 | 105.2 | 105.2 | 300 | 63 | Cu | C | 0 | - | 0 | 20.5 | Between 2 and 5
133 | 287 | 6.8 | overhead | 79.9 | 113.2 | 113.2 | 113.2 | 325 | 63 | Al | C | 0 | - | 0 | 2.7 | Between 2 and 5
133 | 288 | 6.6 | overhead | 79.9 | 113.2 | 113.2 | 113.2 | 325 | 63 | Al | C | 0 | - | 0 | 2.7 | Between 2 and 5
145 | 286 | 0.3 | overhead | 79.9 | 113.2 | 113.2 | 113.2 | 325 | 63 | Al | C | 0 | - | 0 | 20.5 | Between 2 and 5
148 | 172 | 7.6 | overhead | 63 | 71.3 | 71.3 | 71.3 | 325 | 63 | Al | C | 0 | - | 0 | 1.9 | Between 2 and 5
148 | 294 | 12.4 | overhead | 34.2 | 47.8 | 47.8 | 47.8 | 325 | 63 | Al | C | 0 | - | 0 | 2.9 | Between 2 and 5
165 | 272 | 12.9 | overhead | 39.9 | 56.5 | 56.5 | 56.5 | 325 | 63 | Al | C | 0 | - | 0 | 11.2 | Between 2 and 5
165 | 298 | 39.8 | overhead | 39.9 | 56.5 | 56.5 | 56.5 | 325 | 63 | Al | C | 0 | - | 0 | 2 | Between 2 and 5
165 | 300 | 34.1 | overhead | 63 | 71.3 | 71.3 | 71.3 | 325 | 63 | Al | C | 0 | - | 0 | 1.6 | Between 2 and 5
167 | 297 | 2 | overhead | 34.2 | 47.8 | 47.8 | 47.8 | 235 | 63 | Al | C | 0 | - | 0 | 3.2 | Between 2 and 5
172 | 304 | 11.8 | overhead | 63 | 71.3 | 71.3 | 71.3 | 325 | 63 | Al | C | 0 | - | 0 | 2.6 | Between 2 and 5
173 | 174 | 8 | overhead | 274 | 291 | 307 | 322 | Zambeze | 150 | Al | C | 0 | - | 0 | 10.8 | Between 2 and 5
175 | 176 | 10.5 | overhead | 96 | 104 | 104 | 104 | Bear | 150 | Al | C | 15 | - | 0 | 12 | Between 2 and 5
180 | 249 | 4.5 | overhead | 136 | 162 | 183 | 203 | Zebra | 150 | Al | A | 0 | 1 | 4 | 2.7 | Between 2 and 5
185 | 247 | 8.5 | overhead | 171 | 186 | 196 | 206 | Bear | 150 | Al | - | 0 | - | 0 | 0 | Between 2 and 5
186 | 247 | 6.9 | overhead | 171 | 186 | 196 | 206 | Bear | 150 | Al | A | 0 | 1 | 1.8 | 0.6 | Between 2 and 5
190 | 256 | 1.9 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | A | 0 | 1 | 7.6 | 19.6 | Between 2 and 5
193 | 220 | 9.2 | overhead | 1200 | 1200 | 1200 | 1200 | Zambeze | 220 | Al | C | 0 | - | 0 | 11.4 | Between 2 and 5
195 | 258 | 15.1 | overhead | 199 | 237 | 269 | 297 | Zebra | 220 | Al | C | 0 | - | 0 | 18.3 | Between 2 and 5
208 | 210 | 2.6 | overhead | 897 | 941 | 982 | 1021 | Zambeze | 220 | Al | C | 0 | - | 0 | 6.7 | Between 2 and 5
209 | 211 | 2.6 | overhead | 897 | 941 | 982 | 1021 | Zambeze | 220 | Al | C | 0 | - | 0 | 7.5 | Between 2 and 5
212 | 263 | 12.5 | overhead | 374 | 381 | 381 | 381 | Zebra | 220 | Al | C | 0 | - | 0 | 10 | Between 2 and 5
212 | 266 | 0.3 | overhead | 374 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 7 | Between 2 and 5
220 | 221 | 0.8 | overhead | 1204 | 1279 | 1350 | 1416 | Zambeze | 220 | Al | C | 0 | - | 0 | 17.3 | Between 2 and 5
223 | 262 | 13.2 | overhead | 342 | 364 | 383 | 402 | Zebra | 220 | Al | C | 0 | - | 0 | 13.3 | Between 2 and 5
223 | 265 | 0.1 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 7.7 | Between 2 and 5
224 | 264 | 3.6 | overhead | 382 | 400 | 418 | 435 | Zebra | 220 | Al | C | 0 | - | 0 | 17.7 | Between 2 and 5
269 | 270 | 0.1 | overhead | 68.4 | 95.7 | 95.7 | 95.7 | 235 | 63 | Al | C | 0 | - | 0 | 6.5 | Between 2 and 5
270 | 271 | 11 | overhead | 63 | 71.3 | 71.3 | 71.3 | 325 | 63 | Al | C | 0 | - | 0 | 8.4 | Between 2 and 5
271 | 272 | 23.1 | overhead | 63 | 71.3 | 71.3 | 71.3 | 325 | 63 | Al | C | 0 | - | 0 | 8.4 | Between 2 and 5
273 | 274 | 0.7 | overhead | 39.9 | 56.5 | 56.5 | 56.5 | 325 | 63 | Al | C | 15 | - | 0 | 22 | Between 2 and 5
273 | 282 | 0.9 | overhead | 141.9 | 148.1 | 148.1 | 148.1 | 380 | 63 | Al | B | 0 | - | 0 | 16.2 | Between 2 and 5
274 | 275 | 1 | overhead | 39.9 | 56.5 | 56.5 | 56.5 | 325 | 63 | Al | C | 15 | - | 0 | 22 | Between 2 and 5
275 | 276 | 18.9 | overhead | 79.9 | 113.2 | 113.2 | 113.2 | 325 | 63 | Al | C | 0 | - | 0 | 11 | Between 2 and 5
276 | 277 | 0.7 | overhead | 141.9 | 148.1 | 148.1 | 148.1 | 380 | 63 | Al | C | 0 | - | 0 | 7.9 | Between 2 and 5
277 | 278 | 1.6 | overhead | 39.9 | 56.5 | 56.5 | 56.5 | 325 | 63 | Al | C | 15 | - | 0 | 21.9 | Between 2 and 5
278 | 279 | 6.6 | overhead | 79.9 | 113.2 | 113.2 | 113.2 | 325 | 63 | Al | C | 0 | - | 0 | 10.9 | Between 2 and 5
280 | 281 | 3.9 | overhead | 126 | 142.6 | 142.6 | 142.6 | 325 | 63 | Al | B | 15 | - | 0 | 16.9 | Between 2 and 5
281 | 282 | 1.7 | overhead | 141.9 | 148.1 | 148.1 | 148.1 | 380 | 63 | Al | B | 0 | - | 0 | 16.2 | Between 2 and 5
283 | 284 | 18.1 | overhead | 89.5 | 127.8 | 127.8 | 127.8 | 400 | 63 | Al | C | 0 | - | 0 | 18.2 | Between 2 and 5
284 | 285 | 0.3 | overhead | 79.9 | 113.2 | 113.2 | 113.2 | 325 | 63 | Al | C | 0 | - | 0 | 20.5 | Between 2 and 5
285 | 286 | 6.2 | overhead | 89.5 | 127.8 | 127.8 | 127.8 | 400 | 63 | Al | C | 0 | - | 0 | 18.2 | Between 2 and 5
287 | 288 | 0.1 | overhead | 128.1 | 158.8 | 158.8 | 158.8 | 1000 | 63 | Al | C | 0 | - | 0 | 1.7 | Between 2 and 5
287 | 289 | 3.5 | overhead | 53.2 | 60.1 | 60.1 | 60.1 | 235 | 63 | Al | C | 0 | - | 0 | 8.7 | Between 2 and 5
289 | 290 | 3.2 | overhead | 60.6 | 68.5 | 68.5 | 68.5 | 288 | 63 | Al | C | 0 | - | 0 | 7.6 | Between 2 and 5
290 | 291 | 1 | overhead | 62.2 | 76.9 | 76.9 | 76.9 | 630 | 63 | Al | C | 0 | - | 0 | 6.7 | Between 2 and 5
291 | 292 | 0.2 | overhead | 62.2 | 76.9 | 76.9 | 76.9 | 630 | 63 | Al | C | 0 | - | 0 | 6.4 | Between 2 and 5
292 | 293 | 18 | submarine | 80 | 80 | 80 | 80 | 1000 | 63 | Cu | C | 0 | - | 0 | 5.7 | Between 2 and 5
294 | 295 | 15.9 | overhead | 34.2 | 47.8 | 47.8 | 47.8 | 235 | 63 | Al | C | 0 | - | 0 | 3.1 | Between 2 and 5
295 | 296 | 3.3 | overhead | 34.2 | 47.8 | 47.8 | 47.8 | 225 | 63 | Al | C | 0 | - | 0 | 3.1 | Between 2 and 5
296 | 297 | 1.2 | overhead | 34.2 | 47.8 | 47.8 | 47.8 | 235 | 63 | Al | C | 0 | - | 0 | 3.1 | Between 2 and 5
298 | 299 | 0.1 | overhead | 63 | 71.3 | 71.3 | 71.3 | 325 | 63 | Al | C | 0 | - | 0 | 1.1 | Between 2 and 5
299 | 300 | 0.9 | overhead | 75.3 | 93.4 | 93.4 | 93.4 | 1000 | 63 | Al | C | 0 | - | 0 | 1 | Between 2 and 5
299 | 301 | 17.9 | overhead | 63 | 71.3 | 71.3 | 71.3 | 325 | 63 | Al | C | 0 | - | 0 | 2.3 | Between 2 and 5
301 | 302 | 16.8 | overhead | 63 | 71.3 | 71.3 | 71.3 | 325 | 63 | Al | C | 0 | - | 0 | 2.4 | Between 2 and 5
302 | 303 | 19.3 | overhead | 63 | 71.3 | 71.3 | 71.3 | 325 | 63 | Al | C | 0 | - | 0 | 2.5 | Between 2 and 5
303 | 304 | 0.02 | overhead | 63 | 71.3 | 71.3 | 71.3 | 325 | 63 | Al | C | 0 | - | 0 | 2.5 | Between 2 and 5

## Auxiliary Data
Downward | 00:00 - 01:00 | 01:00 - 02:00 | 02:00 - 03:00 | 03:00 - 04:00 | 04:00 - 05:00 | 05:00 - 06:00 | 06:00 - 07:00 | 07:00 - 08:00 | 08:00 - 09:00 | 09:00 - 10:00 | 10:00 - 11:00 | 11:00 - 12:00 | 12:00 - 13:00 | 13:00 - 14:00 | 14:00 - 15:00 | 15:00 - 16:00 | 16:00 - 17:00 | 17:00 - 18:00 | 18:00 - 19:00 | 19:00 - 20:00 | 20:00 - 21:00 | 21:00 - 22:00 | 22:00 - 23:00 | 23:00 - 00:00
Urban | 0.1812% | 0.1129% | 0.06787% | 0.06991% | 0.07075% | 0.1147% | 0.2841% | 0.338% | 0.3094% | 0.2587% | 0.2719% | 0.2362% | 0.3118% | 0.3008% | 0.2268% | 0.2043% | 0.194% | 0.2214% | 0.1995% | 0.1947% | 0.1907% | 0.177% | 0.1853% | 0.1836%
Semi-urban | 0.1757% | 0.1583% | 0.1514% | 0.1585% | 0.1425% | 0.2051% | 0.3837% | 0.4028% | 0.344% | 0.1931% | 0.209% | 0.2298% | 0.3622% | 0.3385% | 0.1957% | 0.1863% | 0.2177% | 0.2639% | 0.1834% | 0.1943% | 0.1769% | 0.1553% | 0.1545% | 0.1402%
Rural | 0.2298% | 0.1194% | 0.03063% | 0.03207% | 0.03307% | 0.06153% | 0.1571% | 0.1814% | 0.2264% | 0.3104% | 0.2939% | 0.2207% | 0.2579% | 0.2898% | 0.2494% | 0.2176% | 0.1895% | 0.1967% | 0.2671% | 0.2743% | 0.2632% | 0.2403% | 0.2888% | 0.2594%
Upward | 00:00 - 01:00 | 01:00 - 02:00 | 02:00 - 03:00 | 03:00 - 04:00 | 04:00 - 05:00 | 05:00 - 06:00 | 06:00 - 07:00 | 07:00 - 08:00 | 08:00 - 09:00 | 09:00 - 10:00 | 10:00 - 11:00 | 11:00 - 12:00 | 12:00 - 13:00 | 13:00 - 14:00 | 14:00 - 15:00 | 15:00 - 16:00 | 16:00 - 17:00 | 17:00 - 18:00 | 18:00 - 19:00 | 19:00 - 20:00 | 20:00 - 21:00 | 21:00 - 22:00 | 22:00 - 23:00 | 23:00 - 00:00
Urban | 0.2343% | 0.2258% | 0.1651% | 0.1699% | 0.1699% | 0.1929% | 0.2685% | 0.2152% | 0.1114% | 0.1593% | 0.1678% | 0.1916% | 0.1075% | 0.08918% | 0.1599% | 0.1595% | 0.1277% | 0.05462% | 0.02146% | 0.0212% | 0.04645% | 0.1553% | 0.2605% | 0.2629%
Semi-urban | 0.06505% | 0.06579% | 0.0606% | 0.06304% | 0.05822% | 0.0648% | 0.08405% | 0.07974% | 0.1064% | 0.2306% | 0.2413% | 0.1852% | 0.057% | 0.098% | 0.2258% | 0.2201% | 0.177% | 0.04429% | 0.04073% | 0.04443% | 0.04839% | 0.06203% | 0.07203% | 0.05832%
Rural | 0.3082% | 0.3331% | 0.3172% | 0.3286% | 0.3358% | 0.3446% | 0.368% | 0.2727% | 0.09782% | 0.05652% | 0.09736% | 0.2216% | 0.167% | 0.1115% | 0.1473% | 0.1485% | 0.137% | 0.0792% | 0.008639% | 0.007898% | 0.04642% | 0.2162% | 0.3727% | 0.3952%
Load per transmission node
Urban | 40%
Semi-urban | 40%
Rural | 20%

## Downward flexibility
Bus \ Hour | 00:00 - 01:00 | 01:00 - 02:00 | 02:00 - 03:00 | 03:00 - 04:00 | 04:00 - 05:00 | 05:00 - 06:00 | 06:00 - 07:00 | 07:00 - 08:00 | 08:00 - 09:00 | 09:00 - 10:00 | 10:00 - 11:00 | 11:00 - 12:00 | 12:00 - 13:00 | 13:00 - 14:00 | 14:00 - 15:00 | 15:00 - 16:00 | 16:00 - 17:00 | 17:00 - 18:00 | 18:00 - 19:00 | 19:00 - 20:00 | 20:00 - 21:00 | 21:00 - 22:00 | 22:00 - 23:00 | 23:00 - 00:00
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 0.021281 | 0.013842 | 0.0093896 | 0.0095588 | 0.008966 | 0.013892 | 0.031872 | 0.040804 | 0.0432 | 0.03623 | 0.037547 | 0.034649 | 0.046956 | 0.044984 | 0.031773 | 0.028835 | 0.029419 | 0.034807 | 0.033199 | 0.034756 | 0.032885 | 0.028536 | 0.028077 | 0.023173
109 | 0.37116 | 0.24142 | 0.16377 | 0.16672 | 0.15638 | 0.24231 | 0.5559 | 0.71168 | 0.75346 | 0.6319 | 0.65484 | 0.60432 | 0.81895 | 0.78454 | 0.55415 | 0.50289 | 0.5131 | 0.60708 | 0.57903 | 0.60618 | 0.57356 | 0.4977 | 0.4897 | 0.40416
110 | 0.23268 | 0.15134 | 0.10267 | 0.10451 | 0.098036 | 0.1519 | 0.34849 | 0.44615 | 0.47234 | 0.39613 | 0.41052 | 0.37885 | 0.51339 | 0.49182 | 0.34739 | 0.31526 | 0.32166 | 0.38057 | 0.36299 | 0.38001 | 0.35956 | 0.31201 | 0.30699 | 0.25337
111 | 0.22087 | 0.14366 | 0.097456 | 0.099211 | 0.093062 | 0.14419 | 0.33081 | 0.42351 | 0.44837 | 0.37603 | 0.38968 | 0.35962 | 0.48734 | 0.46686 | 0.32976 | 0.29926 | 0.30533 | 0.36126 | 0.34457 | 0.36073 | 0.34132 | 0.29618 | 0.29141 | 0.24051
112 | 0.29307 | 0.19062 | 0.12931 | 0.13164 | 0.12348 | 0.19133 | 0.43894 | 0.56195 | 0.59494 | 0.49895 | 0.51706 | 0.47718 | 0.64665 | 0.61947 | 0.43756 | 0.39708 | 0.40514 | 0.47935 | 0.4572 | 0.47864 | 0.45289 | 0.39299 | 0.38667 | 0.31913
113 | 0.10146 | 0.065991 | 0.044766 | 0.045573 | 0.042748 | 0.066235 | 0.15196 | 0.19454 | 0.20596 | 0.17273 | 0.179 | 0.16519 | 0.22386 | 0.21445 | 0.15148 | 0.13746 | 0.14025 | 0.16594 | 0.15828 | 0.1657 | 0.15678 | 0.13605 | 0.13386 | 0.11048
114 | 0.22666 | 0.14743 | 0.10001 | 0.10181 | 0.0955 | 0.14797 | 0.33948 | 0.43461 | 0.46012 | 0.38588 | 0.39989 | 0.36904 | 0.50011 | 0.47909 | 0.3384 | 0.3071 | 0.31333 | 0.37072 | 0.3536 | 0.37018 | 0.35026 | 0.30393 | 0.29904 | 0.24681
115 | 0.083212 | 0.054124 | 0.036716 | 0.037378 | 0.035061 | 0.054324 | 0.12463 | 0.15956 | 0.16892 | 0.14167 | 0.14681 | 0.13548 | 0.1836 | 0.17589 | 0.12424 | 0.11275 | 0.11503 | 0.1361 | 0.12982 | 0.1359 | 0.12859 | 0.11158 | 0.10979 | 0.090611
116 | 0.44842 | 0.29167 | 0.19786 | 0.20142 | 0.18894 | 0.29275 | 0.67162 | 0.85983 | 0.91031 | 0.76344 | 0.79115 | 0.73012 | 0.98943 | 0.94785 | 0.6695 | 0.60757 | 0.61991 | 0.73345 | 0.69956 | 0.73236 | 0.69296 | 0.60131 | 0.59163 | 0.4883
117 | 0.074677 | 0.048572 | 0.032949 | 0.033543 | 0.031464 | 0.048751 | 0.11185 | 0.14319 | 0.15159 | 0.12714 | 0.13175 | 0.12159 | 0.16477 | 0.15785 | 0.11149 | 0.10118 | 0.10323 | 0.12214 | 0.1165 | 0.12196 | 0.1154 | 0.10013 | 0.098525 | 0.081316
118 | 0.16807 | 0.10932 | 0.07416 | 0.075496 | 0.070816 | 0.10973 | 0.25173 | 0.32227 | 0.34119 | 0.28615 | 0.29653 | 0.27366 | 0.37085 | 0.35527 | 0.25094 | 0.22772 | 0.23235 | 0.27491 | 0.2622 | 0.2745 | 0.25973 | 0.22538 | 0.22175 | 0.18302
119 | 0.33938 | 0.22075 | 0.14975 | 0.15244 | 0.14299 | 0.22156 | 0.50831 | 0.65075 | 0.68895 | 0.5778 | 0.59877 | 0.55258 | 0.74884 | 0.71737 | 0.5067 | 0.45983 | 0.46917 | 0.5551 | 0.52945 | 0.55428 | 0.52446 | 0.45509 | 0.44777 | 0.36956
120 | 0.19448 | 0.1265 | 0.08581 | 0.087356 | 0.081941 | 0.12696 | 0.29128 | 0.3729 | 0.39479 | 0.3311 | 0.34312 | 0.31665 | 0.42911 | 0.41108 | 0.29036 | 0.2635 | 0.26885 | 0.31809 | 0.3034 | 0.31762 | 0.30053 | 0.26078 | 0.25659 | 0.21177
121 | 0.16599 | 0.10797 | 0.073241 | 0.07456 | 0.069939 | 0.10836 | 0.24862 | 0.31828 | 0.33697 | 0.2826 | 0.29286 | 0.27027 | 0.36626 | 0.35086 | 0.24783 | 0.2249 | 0.22947 | 0.2715 | 0.25896 | 0.2711 | 0.25651 | 0.22259 | 0.21901 | 0.18075
122 | 0.3098 | 0.20151 | 0.1367 | 0.13916 | 0.13053 | 0.20225 | 0.46401 | 0.59403 | 0.62891 | 0.52744 | 0.54659 | 0.50442 | 0.68357 | 0.65484 | 0.46254 | 0.41976 | 0.42828 | 0.50672 | 0.48331 | 0.50597 | 0.47875 | 0.41543 | 0.40875 | 0.33735
123 | 0.26841 | 0.17459 | 0.11843 | 0.12057 | 0.11309 | 0.17523 | 0.40201 | 0.51467 | 0.54488 | 0.45697 | 0.47356 | 0.43703 | 0.59224 | 0.56735 | 0.40074 | 0.36367 | 0.37106 | 0.43902 | 0.41874 | 0.43837 | 0.41478 | 0.35992 | 0.35413 | 0.29228
124 | 0.18296 | 0.119 | 0.080726 | 0.08218 | 0.077086 | 0.11944 | 0.27402 | 0.35081 | 0.3714 | 0.31148 | 0.32279 | 0.29789 | 0.40368 | 0.38672 | 0.27315 | 0.24789 | 0.25292 | 0.29925 | 0.28542 | 0.2988 | 0.28272 | 0.24533 | 0.24139 | 0.19922
125 | 0.17494 | 0.11379 | 0.077188 | 0.078579 | 0.073708 | 0.1142 | 0.26201 | 0.33543 | 0.35512 | 0.29783 | 0.30864 | 0.28483 | 0.38599 | 0.36977 | 0.26118 | 0.23702 | 0.24184 | 0.28613 | 0.27291 | 0.28571 | 0.27034 | 0.23458 | 0.23081 | 0.19049
126 | 0.12972 | 0.084378 | 0.057239 | 0.058269 | 0.054657 | 0.084688 | 0.19429 | 0.24874 | 0.26334 | 0.22086 | 0.22887 | 0.21122 | 0.28623 | 0.2742 | 0.19368 | 0.17576 | 0.17933 | 0.21218 | 0.20237 | 0.21187 | 0.20047 | 0.17395 | 0.17115 | 0.14126
127 | 0.11467 | 0.074582 | 0.050594 | 0.051505 | 0.048313 | 0.074857 | 0.17174 | 0.21987 | 0.23277 | 0.19522 | 0.2023 | 0.1867 | 0.253 | 0.24237 | 0.1712 | 0.15536 | 0.15852 | 0.18755 | 0.17888 | 0.18727 | 0.17719 | 0.15376 | 0.15128 | 0.12486
128 | 0.43498 | 0.28293 | 0.19193 | 0.19538 | 0.18327 | 0.28397 | 0.65148 | 0.83404 | 0.88301 | 0.74054 | 0.76743 | 0.70822 | 0.95976 | 0.91942 | 0.64942 | 0.58935 | 0.60132 | 0.71145 | 0.67859 | 0.7104 | 0.67218 | 0.58328 | 0.57389 | 0.47365
129 | 0.39332 | 0.25583 | 0.17355 | 0.17667 | 0.16572 | 0.25677 | 0.5891 | 0.75417 | 0.79845 | 0.66963 | 0.69394 | 0.6404 | 0.86785 | 0.83138 | 0.58723 | 0.53291 | 0.54373 | 0.64332 | 0.6136 | 0.64237 | 0.60781 | 0.52742 | 0.51893 | 0.42829
130 | 0.4747 | 0.30877 | 0.20946 | 0.21323 | 0.20001 | 0.3099 | 0.71098 | 0.91022 | 0.96365 | 0.80818 | 0.83752 | 0.77291 | 1.0474 | 1.0034 | 0.70874 | 0.64318 | 0.65624 | 0.77643 | 0.74056 | 0.77528 | 0.73357 | 0.63655 | 0.62631 | 0.51691
131 | 0.20524 | 0.1335 | 0.09056 | 0.092191 | 0.086476 | 0.13399 | 0.3074 | 0.39354 | 0.41664 | 0.34942 | 0.36211 | 0.33417 | 0.45286 | 0.43383 | 0.30643 | 0.27808 | 0.28373 | 0.3357 | 0.32019 | 0.3352 | 0.31716 | 0.27522 | 0.27079 | 0.22349
132 | 0.015161 | 0.0098618 | 0.0066899 | 0.0068103 | 0.0063882 | 0.0098983 | 0.02271 | 0.029072 | 0.030779 | 0.025813 | 0.02675 | 0.024686 | 0.033454 | 0.032047 | 0.022637 | 0.020544 | 0.02096 | 0.024799 | 0.023652 | 0.024762 | 0.023429 | 0.020332 | 0.020005 | 0.01651
133 | 0.1818 | 0.11825 | 0.080216 | 0.081661 | 0.076599 | 0.11869 | 0.27229 | 0.34859 | 0.36906 | 0.30951 | 0.32075 | 0.29601 | 0.40113 | 0.38428 | 0.27143 | 0.24632 | 0.25132 | 0.29736 | 0.28362 | 0.29691 | 0.28094 | 0.24378 | 0.23986 | 0.19796
134 | 0.25271 | 0.16438 | 0.11151 | 0.11351 | 0.10648 | 0.16498 | 0.3785 | 0.48457 | 0.51301 | 0.43024 | 0.44586 | 0.41147 | 0.5576 | 0.53417 | 0.3773 | 0.3424 | 0.34935 | 0.41334 | 0.39425 | 0.41273 | 0.39052 | 0.33887 | 0.33342 | 0.27518
135 | 0.27564 | 0.17929 | 0.12162 | 0.12381 | 0.11614 | 0.17995 | 0.41284 | 0.52853 | 0.55955 | 0.46928 | 0.48631 | 0.4488 | 0.60819 | 0.58263 | 0.41153 | 0.37347 | 0.38105 | 0.45084 | 0.43001 | 0.45018 | 0.42595 | 0.36962 | 0.36367 | 0.30015
136 | 0.31258 | 0.20332 | 0.13792 | 0.14041 | 0.1317 | 0.20406 | 0.46817 | 0.59936 | 0.63455 | 0.53217 | 0.55149 | 0.50895 | 0.6897 | 0.66072 | 0.46669 | 0.42352 | 0.43212 | 0.51127 | 0.48765 | 0.51051 | 0.48304 | 0.41915 | 0.41241 | 0.34038
137 | 0.1751 | 0.11389 | 0.077261 | 0.078653 | 0.073778 | 0.11431 | 0.26226 | 0.33575 | 0.35546 | 0.29811 | 0.30894 | 0.2851 | 0.38636 | 0.37012 | 0.26143 | 0.23725 | 0.24206 | 0.2864 | 0.27317 | 0.28598 | 0.27059 | 0.2348 | 0.23102 | 0.19067
138 | 0.17731 | 0.11533 | 0.078234 | 0.079643 | 0.074706 | 0.11575 | 0.26556 | 0.33998 | 0.35993 | 0.30186 | 0.31282 | 0.28869 | 0.39122 | 0.37478 | 0.26472 | 0.24023 | 0.24511 | 0.29001 | 0.27661 | 0.28958 | 0.274 | 0.23776 | 0.23393 | 0.19307
139 | 0.21819 | 0.14192 | 0.096274 | 0.098007 | 0.091933 | 0.14244 | 0.3268 | 0.41837 | 0.44294 | 0.37147 | 0.38496 | 0.35526 | 0.48143 | 0.4612 | 0.32576 | 0.29563 | 0.30163 | 0.35688 | 0.34039 | 0.35635 | 0.33718 | 0.29258 | 0.28788 | 0.23759
140 | 0.12025 | 0.078213 | 0.053056 | 0.054012 | 0.050664 | 0.0785 | 0.1801 | 0.23057 | 0.2441 | 0.20472 | 0.21215 | 0.19578 | 0.26532 | 0.25417 | 0.17953 | 0.16292 | 0.16623 | 0.19668 | 0.18759 | 0.19639 | 0.18582 | 0.16124 | 0.15865 | 0.13094
141 | 0.15758 | 0.10249 | 0.069527 | 0.07078 | 0.066392 | 0.10287 | 0.23601 | 0.30214 | 0.31988 | 0.26827 | 0.27801 | 0.25656 | 0.34768 | 0.33307 | 0.23526 | 0.2135 | 0.21783 | 0.25773 | 0.24583 | 0.25735 | 0.2435 | 0.2113 | 0.2079 | 0.17159
142 | 0.19062 | 0.12399 | 0.084108 | 0.085623 | 0.080316 | 0.12444 | 0.2855 | 0.3655 | 0.38696 | 0.32453 | 0.33631 | 0.31037 | 0.4206 | 0.40292 | 0.2846 | 0.25827 | 0.26352 | 0.31178 | 0.29738 | 0.31132 | 0.29457 | 0.25561 | 0.2515 | 0.20757
143 | 0.062584 | 0.040707 | 0.027613 | 0.028111 | 0.026369 | 0.040857 | 0.093733 | 0.12 | 0.12704 | 0.10655 | 0.11041 | 0.1019 | 0.13809 | 0.13229 | 0.093436 | 0.084794 | 0.086515 | 0.10236 | 0.097634 | 0.10221 | 0.096711 | 0.083921 | 0.08257 | 0.068147
144 | 0.094782 | 0.061651 | 0.041822 | 0.042575 | 0.039936 | 0.061877 | 0.14196 | 0.18174 | 0.19241 | 0.16137 | 0.16723 | 0.15433 | 0.20913 | 0.20035 | 0.14151 | 0.12842 | 0.13103 | 0.15503 | 0.14787 | 0.1548 | 0.14647 | 0.1271 | 0.12505 | 0.10321
145 | 0.27551 | 0.1792 | 0.12156 | 0.12375 | 0.11608 | 0.17986 | 0.41264 | 0.52827 | 0.55928 | 0.46905 | 0.48607 | 0.44858 | 0.60789 | 0.58235 | 0.41133 | 0.37328 | 0.38086 | 0.45062 | 0.4298 | 0.44995 | 0.42574 | 0.36943 | 0.36349 | 0.3
146 | 0.019947 | 0.012975 | 0.0088013 | 0.0089595 | 0.0084045 | 0.013021 | 0.029875 | 0.038246 | 0.040493 | 0.03396 | 0.035193 | 0.032478 | 0.044011 | 0.042164 | 0.029781 | 0.027027 | 0.027576 | 0.032625 | 0.031117 | 0.032578 | 0.030825 | 0.026748 | 0.026317 | 0.02172
147 | 0.10373 | 0.067472 | 0.045771 | 0.046594 | 0.043707 | 0.06772 | 0.15537 | 0.1989 | 0.21058 | 0.1766 | 0.18302 | 0.1689 | 0.22888 | 0.21926 | 0.15487 | 0.14055 | 0.1434 | 0.16967 | 0.16183 | 0.16942 | 0.1603 | 0.1391 | 0.13686 | 0.11296
149 | 0.19797 | 0.12877 | 0.087349 | 0.088923 | 0.083411 | 0.12924 | 0.2965 | 0.37959 | 0.40187 | 0.33704 | 0.34927 | 0.32233 | 0.43681 | 0.41845 | 0.29557 | 0.26823 | 0.27367 | 0.3238 | 0.30884 | 0.32332 | 0.30592 | 0.26546 | 0.26119 | 0.21557
150 | 0.11224 | 0.073009 | 0.049526 | 0.050419 | 0.047293 | 0.073278 | 0.16811 | 0.21522 | 0.22786 | 0.1911 | 0.19803 | 0.18276 | 0.24766 | 0.23726 | 0.16758 | 0.15208 | 0.15517 | 0.18359 | 0.17511 | 0.18332 | 0.17345 | 0.15051 | 0.14809 | 0.12222
151 | 0.26927 | 0.17514 | 0.11881 | 0.12095 | 0.11345 | 0.17579 | 0.4033 | 0.51631 | 0.54662 | 0.45843 | 0.47508 | 0.43843 | 0.59413 | 0.56917 | 0.40202 | 0.36484 | 0.37224 | 0.44042 | 0.42008 | 0.43977 | 0.41611 | 0.36107 | 0.35527 | 0.29321
152 | 0.1209 | 0.078636 | 0.053344 | 0.054305 | 0.050939 | 0.078927 | 0.18107 | 0.23182 | 0.24543 | 0.20583 | 0.2133 | 0.19685 | 0.26676 | 0.25555 | 0.1805 | 0.16381 | 0.16713 | 0.19774 | 0.18861 | 0.19745 | 0.18683 | 0.16212 | 0.15951 | 0.13165
153 | 0.013067 | 0.0084986 | 0.0057655 | 0.0058697 | 0.0055059 | 0.0085309 | 0.019569 | 0.025054 | 0.026526 | 0.022246 | 0.023054 | 0.021276 | 0.028832 | 0.027621 | 0.019509 | 0.017704 | 0.018064 | 0.021372 | 0.020385 | 0.02134 | 0.020192 | 0.017521 | 0.017239 | 0.014228
154 | 0.12523 | 0.081452 | 0.055253 | 0.056249 | 0.052762 | 0.081751 | 0.18756 | 0.24011 | 0.25421 | 0.2132 | 0.22093 | 0.20389 | 0.2763 | 0.26469 | 0.18696 | 0.16967 | 0.17311 | 0.20482 | 0.19536 | 0.20452 | 0.19351 | 0.16792 | 0.16522 | 0.13636
155 | 0.069725 | 0.045352 | 0.030765 | 0.031319 | 0.029378 | 0.045518 | 0.10443 | 0.13369 | 0.14154 | 0.11871 | 0.12302 | 0.11353 | 0.15385 | 0.14738 | 0.1041 | 0.094471 | 0.09639 | 0.11404 | 0.10878 | 0.11387 | 0.10775 | 0.093496 | 0.091992 | 0.075924
156 | 0.024301 | 0.015806 | 0.010722 | 0.010915 | 0.010239 | 0.015864 | 0.036395 | 0.046595 | 0.04933 | 0.041371 | 0.042873 | 0.039567 | 0.053617 | 0.051364 | 0.036282 | 0.032925 | 0.033594 | 0.039747 | 0.037911 | 0.039687 | 0.037552 | 0.032586 | 0.032061 | 0.026462
157 | 0.11871 | 0.077212 | 0.052378 | 0.053321 | 0.050016 | 0.077496 | 0.17779 | 0.22762 | 0.24098 | 0.2021 | 0.20944 | 0.19328 | 0.26192 | 0.25092 | 0.17723 | 0.16084 | 0.1641 | 0.19416 | 0.18519 | 0.19387 | 0.18344 | 0.15918 | 0.15662 | 0.12926
158 | 0.12684 | 0.082503 | 0.055966 | 0.056975 | 0.053443 | 0.082806 | 0.18998 | 0.24321 | 0.25749 | 0.21595 | 0.22378 | 0.20652 | 0.27987 | 0.26811 | 0.18937 | 0.17186 | 0.17535 | 0.20746 | 0.19788 | 0.20716 | 0.19601 | 0.17009 | 0.16735 | 0.13812
159 | 0.11848 | 0.077068 | 0.052279 | 0.053221 | 0.049922 | 0.077352 | 0.17746 | 0.22719 | 0.24053 | 0.20172 | 0.20904 | 0.19292 | 0.26143 | 0.25045 | 0.1769 | 0.16054 | 0.1638 | 0.1938 | 0.18484 | 0.19351 | 0.1831 | 0.15888 | 0.15633 | 0.12902
160 | 0.12057 | 0.078426 | 0.053201 | 0.05416 | 0.050803 | 0.078715 | 0.18059 | 0.2312 | 0.24477 | 0.20528 | 0.21273 | 0.19632 | 0.26604 | 0.25486 | 0.18002 | 0.16337 | 0.16668 | 0.19721 | 0.1881 | 0.19692 | 0.18632 | 0.16168 | 0.15908 | 0.1313
161 | 0.02683 | 0.017451 | 0.011838 | 0.012051 | 0.011304 | 0.017515 | 0.040184 | 0.051445 | 0.054463 | 0.045677 | 0.047336 | 0.043682 | 0.059196 | 0.05671 | 0.040055 | 0.03635 | 0.037088 | 0.043882 | 0.041854 | 0.043818 | 0.041459 | 0.035976 | 0.035396 | 0.029214
162 | 0.092161 | 0.059945 | 0.040664 | 0.041397 | 0.038831 | 0.060165 | 0.13803 | 0.17671 | 0.18709 | 0.1569 | 0.1626 | 0.15005 | 0.20335 | 0.1948 | 0.1376 | 0.12487 | 0.1274 | 0.15074 | 0.14378 | 0.15052 | 0.14242 | 0.12358 | 0.12159 | 0.10035
163 | 0.0094339 | 0.0061373 | 0.0041627 | 0.0042377 | 0.0039757 | 0.0061594 | 0.01413 | 0.018092 | 0.019152 | 0.016063 | 0.016645 | 0.015363 | 0.020819 | 0.019942 | 0.014087 | 0.012783 | 0.013042 | 0.015431 | 0.014719 | 0.015409 | 0.01458 | 0.012651 | 0.012448 | 0.010273
164 | 0.042421 | 0.027592 | 0.018717 | 0.019055 | 0.017873 | 0.027694 | 0.063535 | 0.081342 | 0.086116 | 0.07222 | 0.074844 | 0.06907 | 0.0936 | 0.089667 | 0.063336 | 0.057477 | 0.058644 | 0.069384 | 0.06618 | 0.069283 | 0.065553 | 0.056883 | 0.055969 | 0.046194
165 | 0.053629 | 0.034882 | 0.023663 | 0.024089 | 0.022596 | 0.035011 | 0.080322 | 0.10283 | 0.10887 | 0.091302 | 0.094618 | 0.087319 | 0.11833 | 0.11336 | 0.080069 | 0.072663 | 0.074137 | 0.087717 | 0.083664 | 0.087588 | 0.082874 | 0.071912 | 0.070756 | 0.058397
166 | 0.16933 | 0.11014 | 0.074715 | 0.076061 | 0.071346 | 0.11055 | 0.25362 | 0.32468 | 0.34374 | 0.28829 | 0.29875 | 0.27571 | 0.37362 | 0.35792 | 0.25281 | 0.22943 | 0.23409 | 0.27696 | 0.26417 | 0.27655 | 0.26167 | 0.22706 | 0.22341 | 0.18439
167 | 0.017309 | 0.011258 | 0.0076377 | 0.0077754 | 0.0072934 | 0.011301 | 0.025925 | 0.03319 | 0.035139 | 0.02947 | 0.03054 | 0.028183 | 0.038191 | 0.036586 | 0.025843 | 0.023452 | 0.023928 | 0.028311 | 0.027003 | 0.02827 | 0.026748 | 0.023211 | 0.022838 | 0.018848
168 | 0.20454 | 0.13304 | 0.090253 | 0.091878 | 0.086183 | 0.13353 | 0.30636 | 0.39221 | 0.41523 | 0.34824 | 0.36088 | 0.33304 | 0.45132 | 0.43236 | 0.30539 | 0.27714 | 0.28277 | 0.33456 | 0.3191 | 0.33406 | 0.31609 | 0.27428 | 0.26987 | 0.22273
169 | 0.036877 | 0.023987 | 0.016271 | 0.016565 | 0.015538 | 0.024074 | 0.055233 | 0.070711 | 0.074859 | 0.062784 | 0.065063 | 0.060043 | 0.081367 | 0.077947 | 0.055058 | 0.049966 | 0.050979 | 0.060317 | 0.057529 | 0.060227 | 0.056987 | 0.04945 | 0.048653 | 0.040156
170 | 0.040653 | 0.026442 | 0.017938 | 0.01826 | 0.017129 | 0.026539 | 0.060887 | 0.077949 | 0.082525 | 0.069209 | 0.071723 | 0.066191 | 0.089698 | 0.085927 | 0.060694 | 0.055081 | 0.056199 | 0.066491 | 0.06342 | 0.066393 | 0.062822 | 0.054512 | 0.053635 | 0.044267
171 | 0.08281 | 0.053863 | 0.036539 | 0.037197 | 0.034891 | 0.054062 | 0.12403 | 0.15878 | 0.16811 | 0.14099 | 0.1461 | 0.13483 | 0.18272 | 0.17504 | 0.12364 | 0.1122 | 0.11448 | 0.13545 | 0.12919 | 0.13525 | 0.12797 | 0.11104 | 0.10926 | 0.090174
172 | 0.037626 | 0.024474 | 0.016602 | 0.016901 | 0.015854 | 0.024565 | 0.056356 | 0.072148 | 0.076383 | 0.064059 | 0.066386 | 0.061264 | 0.083021 | 0.079534 | 0.056178 | 0.05098 | 0.052016 | 0.061542 | 0.0587 | 0.061452 | 0.058145 | 0.050455 | 0.049643 | 0.040973
245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Upward flexibility
Bus \ Hour | 00:00 - 01:00 | 01:00 - 02:00 | 02:00 - 03:00 | 03:00 - 04:00 | 04:00 - 05:00 | 05:00 - 06:00 | 06:00 - 07:00 | 07:00 - 08:00 | 08:00 - 09:00 | 09:00 - 10:00 | 10:00 - 11:00 | 11:00 - 12:00 | 12:00 - 13:00 | 13:00 - 14:00 | 14:00 - 15:00 | 15:00 - 16:00 | 16:00 - 17:00 | 17:00 - 18:00 | 18:00 - 19:00 | 19:00 - 20:00 | 20:00 - 21:00 | 21:00 - 22:00 | 22:00 - 23:00 | 23:00 - 00:00
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
67 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
108 | 0.020455 | 0.019165 | 0.015383 | 0.015533 | 0.015456 | 0.017039 | 0.022912 | 0.021166 | 0.015029 | 0.024955 | 0.027375 | 0.029316 | 0.014501 | 0.013934 | 0.026675 | 0.026211 | 0.021679 | 0.0082607 | 0.0042761 | 0.0045961 | 0.0077766 | 0.020526 | 0.030092 | 0.02651
109 | 0.35675 | 0.33427 | 0.26829 | 0.27092 | 0.26958 | 0.29718 | 0.39962 | 0.36916 | 0.26212 | 0.43524 | 0.47744 | 0.51131 | 0.25291 | 0.24301 | 0.46524 | 0.45713 | 0.3781 | 0.14407 | 0.07458 | 0.080161 | 0.13563 | 0.358 | 0.52484 | 0.46236
110 | 0.22364 | 0.20955 | 0.16819 | 0.16984 | 0.169 | 0.1863 | 0.25052 | 0.23143 | 0.16432 | 0.27285 | 0.2993 | 0.32054 | 0.15855 | 0.15234 | 0.29165 | 0.28657 | 0.23703 | 0.090319 | 0.046754 | 0.050252 | 0.085028 | 0.22443 | 0.32902 | 0.28985
111 | 0.2123 | 0.19892 | 0.15966 | 0.16122 | 0.16042 | 0.17685 | 0.23781 | 0.21968 | 0.15598 | 0.25901 | 0.28412 | 0.30427 | 0.1505 | 0.14461 | 0.27685 | 0.27203 | 0.225 | 0.085736 | 0.044381 | 0.047702 | 0.080714 | 0.21304 | 0.31232 | 0.27514
112 | 0.28169 | 0.26394 | 0.21185 | 0.21392 | 0.21286 | 0.23466 | 0.31554 | 0.29149 | 0.20697 | 0.34367 | 0.37699 | 0.40373 | 0.1997 | 0.19188 | 0.36735 | 0.36095 | 0.29855 | 0.11376 | 0.058888 | 0.063295 | 0.1071 | 0.28268 | 0.41441 | 0.36508
113 | 0.097518 | 0.091372 | 0.073339 | 0.074056 | 0.073689 | 0.081235 | 0.10924 | 0.10091 | 0.071652 | 0.11898 | 0.13051 | 0.13977 | 0.069134 | 0.066426 | 0.12717 | 0.12496 | 0.10335 | 0.039383 | 0.020386 | 0.021912 | 0.037076 | 0.097859 | 0.14347 | 0.12639
114 | 0.21786 | 0.20413 | 0.16384 | 0.16544 | 0.16462 | 0.18148 | 0.24404 | 0.22544 | 0.16007 | 0.26579 | 0.29156 | 0.31224 | 0.15445 | 0.1484 | 0.28411 | 0.27916 | 0.2309 | 0.087982 | 0.045544 | 0.048952 | 0.082828 | 0.21862 | 0.3205 | 0.28235
115 | 0.079981 | 0.074941 | 0.06015 | 0.060739 | 0.060439 | 0.066627 | 0.089593 | 0.082765 | 0.058767 | 0.097579 | 0.10704 | 0.11463 | 0.056702 | 0.054481 | 0.1043 | 0.10249 | 0.084769 | 0.032301 | 0.016721 | 0.017972 | 0.030409 | 0.080261 | 0.11767 | 0.10366
116 | 0.43101 | 0.40385 | 0.32414 | 0.32731 | 0.32569 | 0.35904 | 0.4828 | 0.44601 | 0.31669 | 0.52585 | 0.57682 | 0.61775 | 0.30556 | 0.29359 | 0.56208 | 0.55229 | 0.45681 | 0.17407 | 0.090105 | 0.096848 | 0.16387 | 0.43252 | 0.63409 | 0.55861
117 | 0.071777 | 0.067253 | 0.053979 | 0.054507 | 0.054238 | 0.059791 | 0.080401 | 0.074274 | 0.052738 | 0.08757 | 0.096058 | 0.10287 | 0.050885 | 0.048892 | 0.093604 | 0.091973 | 0.076073 | 0.028987 | 0.015005 | 0.016128 | 0.027289 | 0.072027 | 0.1056 | 0.093026
118 | 0.16155 | 0.15137 | 0.12149 | 0.12268 | 0.12207 | 0.13457 | 0.18096 | 0.16717 | 0.1187 | 0.19709 | 0.2162 | 0.23154 | 0.11453 | 0.11004 | 0.21068 | 0.207 | 0.17122 | 0.065242 | 0.033772 | 0.0363 | 0.06142 | 0.16211 | 0.23766 | 0.20938
119 | 0.32621 | 0.30565 | 0.24532 | 0.24772 | 0.2465 | 0.27174 | 0.3654 | 0.33756 | 0.23968 | 0.39798 | 0.43656 | 0.46753 | 0.23126 | 0.2222 | 0.4254 | 0.41799 | 0.34573 | 0.13174 | 0.068194 | 0.073298 | 0.12402 | 0.32735 | 0.4799 | 0.42278
120 | 0.18693 | 0.17515 | 0.14058 | 0.14195 | 0.14125 | 0.15572 | 0.20939 | 0.19343 | 0.13735 | 0.22806 | 0.25017 | 0.26791 | 0.13252 | 0.12733 | 0.24377 | 0.23952 | 0.19811 | 0.075491 | 0.039078 | 0.042002 | 0.071069 | 0.18758 | 0.275 | 0.24227
121 | 0.15955 | 0.14949 | 0.11999 | 0.12116 | 0.12056 | 0.13291 | 0.17872 | 0.1651 | 0.11723 | 0.19465 | 0.21352 | 0.22867 | 0.11311 | 0.10868 | 0.20806 | 0.20444 | 0.1691 | 0.064434 | 0.033354 | 0.03585 | 0.060659 | 0.16011 | 0.23472 | 0.20678
122 | 0.29778 | 0.27901 | 0.22394 | 0.22613 | 0.22502 | 0.24805 | 0.33356 | 0.30814 | 0.21879 | 0.36329 | 0.39851 | 0.42679 | 0.2111 | 0.20283 | 0.38833 | 0.38156 | 0.3156 | 0.12026 | 0.062251 | 0.06691 | 0.11321 | 0.29882 | 0.43808 | 0.38593
123 | 0.25799 | 0.24173 | 0.19402 | 0.19592 | 0.19495 | 0.21491 | 0.28899 | 0.26697 | 0.18956 | 0.31476 | 0.34527 | 0.36976 | 0.1829 | 0.17573 | 0.33644 | 0.33058 | 0.27343 | 0.10419 | 0.053934 | 0.05797 | 0.098086 | 0.25889 | 0.37955 | 0.33437
124 | 0.17585 | 0.16477 | 0.13225 | 0.13354 | 0.13288 | 0.14649 | 0.19698 | 0.18197 | 0.12921 | 0.21455 | 0.23534 | 0.25204 | 0.12467 | 0.11978 | 0.22933 | 0.22533 | 0.18638 | 0.071019 | 0.036763 | 0.039514 | 0.066858 | 0.17647 | 0.25871 | 0.22791
125 | 0.16815 | 0.15755 | 0.12645 | 0.12769 | 0.12706 | 0.14007 | 0.18835 | 0.17399 | 0.12354 | 0.20514 | 0.22503 | 0.24099 | 0.1192 | 0.11453 | 0.21928 | 0.21546 | 0.17821 | 0.067906 | 0.035151 | 0.037782 | 0.063928 | 0.16873 | 0.24737 | 0.21792
126 | 0.12469 | 0.11683 | 0.093771 | 0.094687 | 0.094219 | 0.10387 | 0.13967 | 0.12903 | 0.091614 | 0.15212 | 0.16687 | 0.17871 | 0.088395 | 0.084932 | 0.1626 | 0.15977 | 0.13215 | 0.050355 | 0.026066 | 0.028017 | 0.047405 | 0.12512 | 0.18344 | 0.1616
127 | 0.11021 | 0.10327 | 0.082885 | 0.083695 | 0.083283 | 0.09181 | 0.12346 | 0.11405 | 0.080979 | 0.13446 | 0.1475 | 0.15796 | 0.078134 | 0.075074 | 0.14373 | 0.14122 | 0.11681 | 0.04451 | 0.02304 | 0.024765 | 0.041902 | 0.1106 | 0.16214 | 0.14284
128 | 0.41809 | 0.39174 | 0.31442 | 0.3175 | 0.31593 | 0.34828 | 0.46833 | 0.43263 | 0.30719 | 0.51008 | 0.55953 | 0.59922 | 0.2964 | 0.28479 | 0.54523 | 0.53573 | 0.44311 | 0.16885 | 0.087403 | 0.093943 | 0.15895 | 0.41955 | 0.61507 | 0.54186
129 | 0.37805 | 0.35423 | 0.28431 | 0.28709 | 0.28567 | 0.31492 | 0.42348 | 0.3912 | 0.27777 | 0.46123 | 0.50594 | 0.54184 | 0.26801 | 0.25752 | 0.49301 | 0.48442 | 0.40068 | 0.15268 | 0.079033 | 0.084947 | 0.14373 | 0.37937 | 0.55617 | 0.48997
130 | 0.45627 | 0.42752 | 0.34314 | 0.34649 | 0.34478 | 0.38009 | 0.5111 | 0.47215 | 0.33525 | 0.55666 | 0.61063 | 0.65395 | 0.32347 | 0.3108 | 0.59502 | 0.58465 | 0.48358 | 0.18427 | 0.095385 | 0.10252 | 0.17347 | 0.45787 | 0.67125 | 0.59135
131 | 0.19727 | 0.18484 | 0.14836 | 0.14981 | 0.14907 | 0.16433 | 0.22098 | 0.20414 | 0.14495 | 0.24068 | 0.26401 | 0.28274 | 0.13985 | 0.13438 | 0.25726 | 0.25278 | 0.20908 | 0.079669 | 0.04124 | 0.044327 | 0.075002 | 0.19796 | 0.29022 | 0.25567
132 | 0.014573 | 0.013655 | 0.01096 | 0.011067 | 0.011012 | 0.01214 | 0.016325 | 0.01508 | 0.010708 | 0.01778 | 0.019504 | 0.020886 | 0.010331 | 0.0099264 | 0.019005 | 0.018675 | 0.015446 | 0.0058855 | 0.0030465 | 0.0032745 | 0.0055404 | 0.014625 | 0.02144 | 0.018887
133 | 0.17474 | 0.16373 | 0.13141 | 0.1327 | 0.13204 | 0.14556 | 0.19574 | 0.18082 | 0.12839 | 0.21319 | 0.23386 | 0.25045 | 0.12388 | 0.11903 | 0.22788 | 0.22391 | 0.1852 | 0.07057 | 0.03653 | 0.039264 | 0.066435 | 0.17535 | 0.25707 | 0.22647
134 | 0.2429 | 0.2276 | 0.18267 | 0.18446 | 0.18355 | 0.20234 | 0.27209 | 0.25135 | 0.17847 | 0.29635 | 0.32507 | 0.34814 | 0.1722 | 0.16546 | 0.31677 | 0.31125 | 0.25744 | 0.098097 | 0.050779 | 0.05458 | 0.09235 | 0.24375 | 0.35735 | 0.31481
135 | 0.26494 | 0.24824 | 0.19925 | 0.20119 | 0.2002 | 0.2207 | 0.29677 | 0.27416 | 0.19466 | 0.32323 | 0.35457 | 0.37972 | 0.18782 | 0.18047 | 0.3455 | 0.33948 | 0.2808 | 0.107 | 0.055386 | 0.059531 | 0.10073 | 0.26587 | 0.38977 | 0.34337
136 | 0.30045 | 0.28151 | 0.22595 | 0.22816 | 0.22703 | 0.25028 | 0.33655 | 0.3109 | 0.22075 | 0.36655 | 0.40209 | 0.43061 | 0.213 | 0.20465 | 0.39181 | 0.38498 | 0.31843 | 0.12134 | 0.062809 | 0.06751 | 0.11423 | 0.3015 | 0.44201 | 0.38939
137 | 0.1683 | 0.1577 | 0.12657 | 0.12781 | 0.12718 | 0.1402 | 0.18853 | 0.17416 | 0.12366 | 0.20534 | 0.22524 | 0.24122 | 0.11932 | 0.11464 | 0.21949 | 0.21566 | 0.17838 | 0.06797 | 0.035185 | 0.037818 | 0.063988 | 0.16889 | 0.2476 | 0.21813
138 | 0.17042 | 0.15968 | 0.12817 | 0.12942 | 0.12878 | 0.14197 | 0.1909 | 0.17635 | 0.12522 | 0.20792 | 0.22808 | 0.24426 | 0.12082 | 0.11609 | 0.22225 | 0.21837 | 0.18062 | 0.068826 | 0.035627 | 0.038293 | 0.064793 | 0.17102 | 0.25072 | 0.22088
139 | 0.20972 | 0.19651 | 0.15772 | 0.15926 | 0.15848 | 0.1747 | 0.23492 | 0.21702 | 0.15409 | 0.25587 | 0.28067 | 0.30058 | 0.14868 | 0.14286 | 0.2735 | 0.26873 | 0.22227 | 0.084697 | 0.043843 | 0.047124 | 0.079735 | 0.21045 | 0.30853 | 0.27181
140 | 0.11558 | 0.10829 | 0.086919 | 0.087769 | 0.087336 | 0.096278 | 0.12947 | 0.1196 | 0.084921 | 0.14101 | 0.15468 | 0.16565 | 0.081937 | 0.078727 | 0.15072 | 0.1481 | 0.1225 | 0.046676 | 0.024162 | 0.02597 | 0.043942 | 0.11598 | 0.17003 | 0.14979
141 | 0.15146 | 0.14191 | 0.1139 | 0.11502 | 0.11445 | 0.12617 | 0.16966 | 0.15673 | 0.11128 | 0.18478 | 0.20269 | 0.21708 | 0.10737 | 0.10317 | 0.19751 | 0.19407 | 0.16052 | 0.061166 | 0.031663 | 0.034032 | 0.057583 | 0.15199 | 0.22282 | 0.1963
142 | 0.18322 | 0.17167 | 0.13779 | 0.13914 | 0.13845 | 0.15263 | 0.20523 | 0.18959 | 0.13462 | 0.22353 | 0.2452 | 0.2626 | 0.12989 | 0.1248 | 0.23893 | 0.23477 | 0.19418 | 0.073994 | 0.038303 | 0.041169 | 0.069659 | 0.18386 | 0.26955 | 0.23746
143 | 0.060154 | 0.056364 | 0.045238 | 0.045681 | 0.045455 | 0.050109 | 0.067381 | 0.062246 | 0.044198 | 0.073388 | 0.080502 | 0.086215 | 0.042645 | 0.040975 | 0.078445 | 0.077078 | 0.063753 | 0.024293 | 0.012575 | 0.013516 | 0.02287 | 0.060364 | 0.088495 | 0.077961
144 | 0.091102 | 0.085363 | 0.068514 | 0.069184 | 0.068843 | 0.075891 | 0.10205 | 0.094273 | 0.066938 | 0.11115 | 0.12192 | 0.13057 | 0.064586 | 0.062057 | 0.11881 | 0.11674 | 0.096555 | 0.036792 | 0.019046 | 0.020471 | 0.034637 | 0.091422 | 0.13403 | 0.11807
145 | 0.26481 | 0.24812 | 0.19915 | 0.2011 | 0.2001 | 0.22059 | 0.29663 | 0.27402 | 0.19457 | 0.32307 | 0.35439 | 0.37954 | 0.18773 | 0.18038 | 0.34534 | 0.33932 | 0.28066 | 0.10694 | 0.055359 | 0.059502 | 0.10068 | 0.26573 | 0.38958 | 0.3432
146 | 0.019173 | 0.017965 | 0.014419 | 0.014559 | 0.014488 | 0.01597 | 0.021476 | 0.019839 | 0.014087 | 0.023391 | 0.025659 | 0.027479 | 0.013592 | 0.01306 | 0.025003 | 0.024568 | 0.020321 | 0.0077427 | 0.0040079 | 0.0043081 | 0.0072893 | 0.01924 | 0.028205 | 0.024848
147 | 0.099706 | 0.093423 | 0.074984 | 0.075716 | 0.075343 | 0.083056 | 0.11169 | 0.10317 | 0.073258 | 0.12164 | 0.13344 | 0.1429 | 0.070685 | 0.067916 | 0.13003 | 0.12776 | 0.10567 | 0.040266 | 0.020844 | 0.022404 | 0.037907 | 0.10005 | 0.14668 | 0.12922
149 | 0.19028 | 0.17829 | 0.1431 | 0.1445 | 0.14379 | 0.15851 | 0.21315 | 0.1969 | 0.13981 | 0.23215 | 0.25465 | 0.27272 | 0.1349 | 0.12961 | 0.24814 | 0.24382 | 0.20167 | 0.076845 | 0.039779 | 0.042756 | 0.072343 | 0.19095 | 0.27994 | 0.24661
150 | 0.10789 | 0.10109 | 0.081136 | 0.08193 | 0.081525 | 0.089873 | 0.12085 | 0.11164 | 0.07927 | 0.13162 | 0.14439 | 0.15463 | 0.076485 | 0.073489 | 0.14069 | 0.13824 | 0.11434 | 0.043571 | 0.022554 | 0.024242 | 0.041018 | 0.10826 | 0.15872 | 0.13983
151 | 0.25882 | 0.24251 | 0.19464 | 0.19655 | 0.19558 | 0.2156 | 0.28992 | 0.26782 | 0.19017 | 0.31576 | 0.34637 | 0.37095 | 0.18348 | 0.1763 | 0.33752 | 0.33164 | 0.27431 | 0.10452 | 0.054106 | 0.058155 | 0.0984 | 0.25972 | 0.38076 | 0.33544
152 | 0.1162 | 0.10888 | 0.087391 | 0.088246 | 0.087809 | 0.096801 | 0.13017 | 0.12025 | 0.085382 | 0.14177 | 0.15552 | 0.16655 | 0.082381 | 0.079154 | 0.15154 | 0.1489 | 0.12316 | 0.046929 | 0.024293 | 0.026111 | 0.04418 | 0.11661 | 0.17095 | 0.15061
153 | 0.012559 | 0.011767 | 0.0094454 | 0.0095382 | 0.0094911 | 0.010463 | 0.014068 | 0.012996 | 0.0092282 | 0.015323 | 0.016808 | 0.018001 | 0.0089041 | 0.0085554 | 0.016379 | 0.016093 | 0.013311 | 0.0050722 | 0.0026256 | 0.002822 | 0.004775 | 0.012603 | 0.018476 | 0.016277
154 | 0.12036 | 0.11278 | 0.090518 | 0.091405 | 0.090952 | 0.10027 | 0.13483 | 0.12455 | 0.088437 | 0.14685 | 0.16108 | 0.17251 | 0.08533 | 0.081987 | 0.15697 | 0.15423 | 0.12757 | 0.048609 | 0.025162 | 0.027045 | 0.045761 | 0.12078 | 0.17707 | 0.156
155 | 0.067018 | 0.062794 | 0.050402 | 0.050894 | 0.050642 | 0.055827 | 0.07507 | 0.06935 | 0.049242 | 0.081763 | 0.08969 | 0.096054 | 0.047512 | 0.04565 | 0.087398 | 0.085875 | 0.07103 | 0.027065 | 0.01401 | 0.015059 | 0.02548 | 0.067252 | 0.098594 | 0.086858
156 | 0.023357 | 0.021885 | 0.017566 | 0.017737 | 0.01765 | 0.019457 | 0.026163 | 0.02417 | 0.017161 | 0.028496 | 0.031258 | 0.033477 | 0.016558 | 0.01591 | 0.030461 | 0.029929 | 0.024755 | 0.009433 | 0.004883 | 0.0052482 | 0.0088801 | 0.023439 | 0.034362 | 0.030273
157 | 0.1141 | 0.10691 | 0.085808 | 0.086646 | 0.086219 | 0.095047 | 0.12781 | 0.11807 | 0.083834 | 0.1392 | 0.1527 | 0.16353 | 0.080889 | 0.07772 | 0.1488 | 0.1462 | 0.12093 | 0.046079 | 0.023853 | 0.025638 | 0.043379 | 0.1145 | 0.16786 | 0.14788
158 | 0.12192 | 0.11423 | 0.091687 | 0.092584 | 0.092126 | 0.10156 | 0.13657 | 0.12616 | 0.089578 | 0.14874 | 0.16316 | 0.17474 | 0.086431 | 0.083045 | 0.15899 | 0.15622 | 0.12921 | 0.049236 | 0.025487 | 0.027394 | 0.046351 | 0.12234 | 0.17936 | 0.15801
159 | 0.11388 | 0.10671 | 0.085646 | 0.086484 | 0.086057 | 0.094869 | 0.12757 | 0.11785 | 0.083677 | 0.13894 | 0.15241 | 0.16322 | 0.080737 | 0.077575 | 0.14852 | 0.14593 | 0.1207 | 0.045993 | 0.023808 | 0.02559 | 0.043298 | 0.11428 | 0.16754 | 0.1476
160 | 0.11589 | 0.10859 | 0.087156 | 0.088009 | 0.087575 | 0.096541 | 0.12982 | 0.11993 | 0.085152 | 0.14139 | 0.1551 | 0.1661 | 0.08216 | 0.078942 | 0.15113 | 0.1485 | 0.12283 | 0.046803 | 0.024228 | 0.026041 | 0.044061 | 0.1163 | 0.1705 | 0.1502
161 | 0.025788 | 0.024163 | 0.019393 | 0.019583 | 0.019486 | 0.021481 | 0.028886 | 0.026685 | 0.018947 | 0.031462 | 0.034512 | 0.036959 | 0.018281 | 0.017566 | 0.033629 | 0.033043 | 0.02733 | 0.010414 | 0.0053908 | 0.0057945 | 0.0098041 | 0.025878 | 0.037936 | 0.033421
162 | 0.088583 | 0.083001 | 0.066617 | 0.067269 | 0.066937 | 0.073791 | 0.099227 | 0.091665 | 0.065086 | 0.10807 | 0.11855 | 0.12696 | 0.062799 | 0.060339 | 0.11552 | 0.11351 | 0.093883 | 0.035774 | 0.018518 | 0.019904 | 0.033678 | 0.088892 | 0.13032 | 0.11481
163 | 0.0090676 | 0.0084978 | 0.0068196 | 0.0068863 | 0.0068534 | 0.0075543 | 0.010157 | 0.0093845 | 0.0066628 | 0.011064 | 0.012136 | 0.012998 | 0.0064294 | 0.0061768 | 0.011827 | 0.011619 | 0.009611 | 0.0036622 | 0.0018958 | 0.0020377 | 0.0034478 | 0.0090997 | 0.013341 | 0.011752
164 | 0.040774 | 0.038204 | 0.030664 | 0.030965 | 0.03081 | 0.033965 | 0.045673 | 0.042193 | 0.029959 | 0.049745 | 0.054569 | 0.05844 | 0.028906 | 0.027774 | 0.053174 | 0.052247 | 0.043215 | 0.016467 | 0.008524 | 0.0091619 | 0.015502 | 0.040916 | 0.059985 | 0.052846
165 | 0.051547 | 0.048298 | 0.038765 | 0.039144 | 0.038952 | 0.04294 | 0.057741 | 0.05334 | 0.037874 | 0.062888 | 0.068986 | 0.07388 | 0.036544 | 0.035112 | 0.067223 | 0.066051 | 0.054632 | 0.020817 | 0.010776 | 0.011583 | 0.019598 | 0.051727 | 0.075833 | 0.066806
166 | 0.16276 | 0.1525 | 0.1224 | 0.1236 | 0.12299 | 0.13558 | 0.18231 | 0.16842 | 0.11959 | 0.19857 | 0.21782 | 0.23327 | 0.11539 | 0.11086 | 0.21225 | 0.20855 | 0.1725 | 0.06573 | 0.034025 | 0.036571 | 0.061879 | 0.16333 | 0.23944 | 0.21094
167 | 0.016637 | 0.015588 | 0.012512 | 0.012635 | 0.012572 | 0.01386 | 0.018637 | 0.017216 | 0.012225 | 0.020299 | 0.022266 | 0.023845 | 0.011794 | 0.011332 | 0.021697 | 0.021318 | 0.017632 | 0.0067188 | 0.003478 | 0.0037384 | 0.0063252 | 0.016696 | 0.024477 | 0.021562
168 | 0.1966 | 0.18421 | 0.14786 | 0.1493 | 0.14856 | 0.16378 | 0.22023 | 0.20344 | 0.14445 | 0.23986 | 0.26311 | 0.28178 | 0.13938 | 0.13392 | 0.25639 | 0.25192 | 0.20837 | 0.079399 | 0.041101 | 0.044176 | 0.074747 | 0.19729 | 0.28924 | 0.25481
169 | 0.035445 | 0.033212 | 0.026656 | 0.026918 | 0.026785 | 0.029526 | 0.039705 | 0.036679 | 0.026043 | 0.043245 | 0.047437 | 0.050802 | 0.025128 | 0.024144 | 0.046224 | 0.045419 | 0.037566 | 0.014315 | 0.0074098 | 0.0079644 | 0.013476 | 0.03557 | 0.052145 | 0.045939
170 | 0.039075 | 0.036612 | 0.029386 | 0.029673 | 0.029527 | 0.03255 | 0.043769 | 0.040433 | 0.02871 | 0.047671 | 0.052293 | 0.056004 | 0.027701 | 0.026616 | 0.050956 | 0.050069 | 0.041413 | 0.01578 | 0.0081686 | 0.0087798 | 0.014856 | 0.039211 | 0.057484 | 0.050642
171 | 0.079595 | 0.07458 | 0.059859 | 0.060445 | 0.060145 | 0.066305 | 0.089159 | 0.082365 | 0.058483 | 0.097109 | 0.10652 | 0.11408 | 0.056428 | 0.054217 | 0.1038 | 0.10199 | 0.084359 | 0.032145 | 0.01664 | 0.017885 | 0.030262 | 0.079873 | 0.1171 | 0.10316
172 | 0.036165 | 0.033887 | 0.027199 | 0.027464 | 0.02733 | 0.030128 | 0.040512 | 0.037424 | 0.026573 | 0.044123 | 0.048402 | 0.051835 | 0.025639 | 0.024635 | 0.047165 | 0.046341 | 0.038331 | 0.014606 | 0.0075607 | 0.0081264 | 0.01375 | 0.036292 | 0.053206 | 0.046873
245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
247 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
249 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
257 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
259 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
261 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0